# Machine Learning-Based Predictive Maintenance for Solar Mini-Grids

Takudzwa Kelvin Mukaro

C21145793S

Chinhoyi University of Technology

SCHOOL OF ENGINEERING SCIENCES AND TECHNOLOGY

DEPARTMENT OF ICT AND ELECTRONICS

(COMPUTER ENGINEERING)

Title:

Design and Implementation of a Predictive Maintenance System for Solar Mini-Grids using Machine Learning and IoT.

This project is submitted in partial fulfillment of the requirements for the Bachelor of Engineering Honours Degree in Computer Engineering.

# CHAPTER 1: INTRODUCTION

## 1.1 Introduction

Zimbabwe faces a structural energy deficit that has forced a rapid and largely unmanaged expansion of decentralised solar mini-grids. National electricity demand is estimated at 4,000 megawatts (MW) while installed generation capacity stands at approximately 1,400 MW, showing a gap of 2,600 MW that ageing thermal plants and hydrological constraints at hydroelectric facilities cannot close in the near term (Veritas Zimbabwe, 2025). Households, commercial farmers, and Small-to-Medium Enterprises (SMEs) have responded by investing in standalone solar photovoltaic (PV) systems with battery storage as a main power source rather than a supplement.

The hardware has arrived considerably faster than the maintenance knowledge and systems needed to protect it. Most installations operate without any automated health monitoring. Operators rely either on reactive maintenance, which is waiting for a component to fail before acting, or on infrequent manual inspections that cannot detect the gradual internal deterioration of battery banks and inverters (Ministry of Energy and Power Development, 2025). The result is a cycle of unexpected failures, costly emergency replacements, and eroding confidence in solar as a reliable energy source.

This research designs and implements a predictive maintenance system using low-cost ESP32 microcontrollers and a dual-model ML architecture that is the Random Forest regression for battery State of Health (SoH) estimation and Isolation Forest for unsupervised anomaly detection deployed in a server-side configuration. The complete software stack is Docker-containerised, enabling identical deployment across the development laptop used for proof-of-concept, a Raspberry Pi 4 for local edge production, or a cloud Virtual Private Server (VPS) for multi-site monitoring, without any modification to application code. The system is built around the operational realities of Zimbabwean deployments: intermittent internet connectivity, budget-constrained hardware, and limited access to nearby technical expertise.

## 1.2 Background of the Study

## The global photovoltaic capacity milestone of two terawatts was surpassed in 2024, and this reflects the scale of investment committed to solar technology (SolarPower Europe, 2025), yet capacity installation and operational reliability are distinct problems. A comprehensive review by Vichare and Gaikwad (2025) covering 122 peer-reviewed studies found that the dominant research paradigm assumes continuous cloud connectivity, industrial sensor networks, and large historical datasets from utility-scale operations, which are assumptions that exclude the decentralised, off-grid installations that serve the majority of solar energy users across sub-Saharan Africa.
In Zimbabwe, the energy deficit has made a huge change in the role of solar mini-grids fundamentally because what began as an off-grid supplement for remote communities is now a main energy source for urban SMEs, commercial farms, and households that cannot rely on the national grid. Battery banks undergo certain conditions like daily charge-discharge cycling, frequently beyond recommended Depth of Discharge (DoD) limits, under ambient temperatures that accelerate electrochemical degradation. Inverters face variable and excessive load profiles. Panel soiling and partial shading compound result in output losses that would be detectable through continuous parameter monitoring but are invisible to infrequent visual checks (Patabo et al., 2024).
The current technology was created for a different operational environment so this means the monitoring gap is more of an architectural and contextual issue than a technological one. Although SCADA systems work well at utility scale, a five-kilowatt home installation cannot afford the proprietary infrastructure and capital investment they require (Fortune Business Insights, 2024), and this research is on whether predictive maintenance can be made practically deployable under the hardware, connectivity, and economic constraints of decentralised mini-grids in Zimbabwe.

## 1.3 Statement of the Problem

Decentralized solar mini-grids in Zimbabwe operate without an active, automated health monitoring system. The reactive fault rectification approach  combined with infrequent manual inspection  cannot detect early-stage anomalies such as battery sulfation, abnormal discharge rates, inverter thermal stress, and partial shading effects (Ministry of Energy and Power Development, 2025). Which creates the following monitoring gap consequences:

- SMEs without warning mechanisms to intervene before failure can experience unexpected system downtime which disrupts operations.

- Unmanaged deep-cycling and thermally degradation shortens battery bank lifespan, converting a capital investment into a recurring replacement cost (Fracttal Tech S.L., 2026).

- Because there is no performance data, it is impossible to distinguish normal environmental variation from genuine equipment degradation and this can prevent rational maintenance scheduling.

- End-users in rural and peri-urban areas lack proximate technical expertise; the interval between fault onset and rectification is determined by distance to a technician, not fault severity.

Industrial-grade SCADA systems can address these problems but are prohibitively expensive for small-scale deployment (Fortune Business Insights, 2024). A lightweight, affordable, and locally deployable predictive monitoring architecture suited to intermittent-connectivity environments does not currently exist in validated form for this application context.

## 1.4 Aim and Objectives

### 1.4.1 Main Objective

To design and implement a low-cost predictive maintenance system using Machine Learning and IoT sensors, capable of real-time monitoring, anomaly detection, and battery State of Health prediction for decentralised solar mini-grids operating in resource-constrained, intermittent-connectivity environments.

### 1.4.2 Specific Objectives

- To design and simulate a behavioural operational dataset for solar mini-grids incorporating photovoltaic output, inverter load, battery voltage, current, and ambient temperature parameters, with contextual fault injection and sensor-specific Gaussian noise to bridge the simulation-to-real-world gap.

- To develop a firmware-level Store and Forward data acquisition module on the ESP32 microcontroller using LittleFS local buffering and a DS3231 real-time clock module for offline timestamping, ensuring both data and temporal integrity during periods of network unavailability.

- To implement and train a Random Forest regression model for battery State of Health estimation and an Isolation Forest model for multivariate anomaly detection, using the simulated and acquired dataset.

- To develop an integrated, Docker-containerised backend comprising a Python/FastAPI ML microservice and a Node.js/Express telemetry ingestion layer, connected to a React Progressive Web App (PWA) dashboard, deployable without code modification on a development laptop, Raspberry Pi 4, or cloud VPS.

- To evaluate system performance using accuracy, precision, recall, F1-score, and Root Mean Square Error (RMSE), and to benchmark ML-based detection against a static-threshold baseline algorithm under varying operational and fault-injected conditions.

## 1.5 Significance of the Study

### 1.5.1 Economic and Social Impact

In a small-scale solar installation battery banks represent the largest capital investment and their premature failure is the most commercially damaging maintenance event an operator can face. By continuously estimating the battery’s State of Health and flagging all abusive discharge patterns before they cause any permanent electrochemical damage, this system directly protects the investment made by households and SMEs in an environment where Zimbabwe's 2,600 MW supply deficit makes solar the suitable primary energy option for large population segments (Veritas Zimbabwe, 2025). Structured predictive maintenance programmes reduce overall maintenance expenditure by up to 30% and extend component lifespan by approximately 20% (Sigma Technology, 2025).

### 1.5.2 Industry Contribution

This research provides a technically validated prototype for the Zimbabwean solar installation industry that enables a transition from reactive maintenance to proactive, condition-based service delivery. The system reduces Mean Time to Repair (MTTR) by detecting fault precursors before they cause system trips. The Docker-containerised deployment architecture allows solar installers to serve multiple client sites from a single cloud server, amortising infrastructure cost across a client portfolio rather than per site.

### 1.5.3 Academic Contribution

This research makes a specific empirical contribution to Industrial IoT (IIoT) in the Global South. The existing literature, as reviewed by Vichare and Gaikwad (2025) across 122 papers, is dominated by utility-scale deployments with stable infrastructure. The hybrid NTP/DS3231 timekeeping architecture, the sensor-noise-aware simulation methodology, the ACS712 auto-zero compensation design, and a Docker-containerised platform-agnostic deployment approach collectively address specific and identified gaps in the embedded systems and IoT-based predictive maintenance literature.

### 1.5.4 Economic Analysis

To evaluate whether this system satisfies its low-cost design objective, Table 1.1 presents the total cost of ownership under both deployment scenarios which are contextualised against the capital value of the asset being protected.

Table 1.1: Total Cost of Ownership Under Cloud and Local Edge Deployment Scenarios

| Component | Cloud Deployment | Local Edge Deployment | Notes |
| --- | --- | --- | --- |
| ESP32 + sensor array (per node) | ~$25–$30 | ~$25–$30 | PZEM-004T, ACS712, BH1750, DS3231, breadboard |
| Server hardware | $0 (cloud VPS share ~$5–10/month across 50+ client nodes) | $35 (Raspberry Pi 4, 1GB, official MSRP) | Pi 4 confirmed at $35 by Raspberry Pi Ltd. (2025) |
| Total first-year cost per node | ~$37.20 | ~$60–$65 | Pi 4 shared across multiple nodes reduces per-node cost further |
| Annual recurring cost | ~$1.20 | $0 | Pi 4 is a one-time purchase |
| Asset being protected | $2,000–$3,000 (lithium battery bank for 5kW system) | $2,000–$3,000 | Battery bank is the dominant capital cost in a mini-grid |
| Cost as % of protected asset | ~1.5% | ~2.5% | Both satisfy the engineering economics standard for capital asset protection |

Framing the total deployment cost as a fraction of the protected asset value provides the most meaningful economic evaluation. A lithium battery bank for a typical 5kW installation costs approximately $2,000–$3,000 which directly represents the single largest capital investment in the system. At approximately 1.5% (cloud scenario) or 2.5% (local edge scenario) of the protected asset value, the system satisfies the standard engineering economic definition of a rational protective investment, analogous to an insurance premium on capital equipment. This cost-benefit framing provides the quantitative basis for the low-cost claim made throughout this thesis.

## 1.6 Scope and Delimitations

### 1.6.1 Scope

The scope encompasses the full design, implementation, and laboratory evaluation of a prototype predictive maintenance system for standalone solar mini-grids, including: ESP32 IoT sensor node development with DS3231 RTC integration; parametric behavioural data simulation with sensor noise injection; ML model training and evaluation; Docker-containerised full-stack web application development; and benchmarking against static threshold monitoring.

### 1.6.2 Delimitations

- Data generation is limited to parametric behavioural simulation rather than a physics-based Single-Diode Model, due to the latter's computational complexity and reduced flexibility for manual fault injection.

- Physical hardware testing is restricted to a laboratory-controlled environment below 50V, in compliance with undergraduate safety protocols. Full commercial high-voltage deployment falls outside scope.

- Predictive models target Lead-Acid and Lithium-Ion (LiFePO4) chemistries, which dominate the Zimbabwean household and SME solar market. Niche technologies such as flow batteries are excluded.

- Physical structural inspection approaches, including UAV-based thermographic imaging for PV panel micro-cracks  are explicitly out of scope.

- Server Deployment Architecture: The prototype uses a development laptop running the server stack on localhost as the Proof of Concept (PoC) host. In the same way that a compiler runs on an engineer's workstation during development but the compiled binary executes on target hardware in production, the laptop validates software architecture without constraining the production deployment target. The complete server stack is Docker-containerised; a Docker image validated on the development laptop runs without modification on any Docker-enabled host such as cloud VPS or Raspberry Pi 4 as confirmed by Docker's multi-platform documentation (Docker Documentation, 2025) and a peer-reviewed Scientific Reports IoT deployment study using FastAPI, Docker, and Raspberry Pi 4 (Hashim et al., 2025). Commercial deployment would use a cloud VPS at approximately $5–10/month for sites with GSM coverage, or a Raspberry Pi 4 at $35 official MSRP (Raspberry Pi Ltd., 2025) for deep-rural zero-connectivity sites.

## 1.7 Limitations

- The scarcity of long-term historical fault data from local mini-grid installations is a foundational constraint. ML models must initially be trained on synthetic data. To bridge the simulation-to-real-world gap, the simulation engine injects sensor-specific Gaussian noise calibrated to hardware datasheets: ±1.5% on current readings (ACS712 total output error at 25°C per Allegro MicroSystems, 2024), ±0.5% on voltage and power readings (PZEM-004T measurement accuracy per PEACEFAIR, 2023), and ±2 lux on illuminance readings (BH1750 typical accuracy). This prevents models from overfitting to more clean data for simulation.

- The ACS712 exhibits temperature-dependent quiescent output (Q-point) voltage drift which means that ambient temperature rises in Zimbabwe's summer peaks of 38–42°C can introduce systematic measurement error that a fixed calibration constant cannot correct, this is when the sensor's zero-current baseline shifts (Allegro MicroSystems, 2024). The firmware addresses this through a software auto-zero calibration routine that is executed during known open-circuit states identified by the charge controller state output. Ambient temperature is also fed as a model feature to provide implicit residual thermal compensation via Random Forest's non-linear learning.

- The ESP32 resets to epoch time (1 January 1970) on power loss that happens without NTP access (Last Minute Engineers, 2024). This is resolved by the use of a DS3231 TCXO RTC module backed by a CR2032 coin cell. This mechanism maintains accurate timekeeping independent of the ESP32 power state. Once the connectivity is restored, the Node.js backend performs a monotonicity check on buffered timestamps before flushing to MySQL, thus providing a two-stage timestamp integrity check.

- The system only measures battery surface temperature rather than internal core temperature. Internal temperature of the battery during high-rate discharge can exceed the surface temperature by several degrees Celsius due to the resistive and electrochemical heat generation (Raijmakers et al., 2022). Random Forest ensemble methods are robust to the estimation of SoH from externally measurable surface parameters (Abdulla et al., 2024). This limitation is most significant during high-rate discharge events and it is identified as an area for future validation.

- LittleFS distributes 288 daily writes across approximately 64 NOR flash sectors via wear levelling at a five-minute logging interval yielding a theoretical flash lifespan of 22,222 days (approximately 60 years) before sector endurance limits are even reached. The practical storage constraint is not flash endurance but rather log file rotation and size management (Espressif Systems, 2024).

## 1.8 Definition of Terms

Predictive Maintenance (PdM): A proactive maintenance strategy that employs continuous data acquisition and analytical algorithms to forecast equipment failure before it occurs while enabling planned intervention which minimizes unplanned downtime and reduces repair costs.

Solar Mini-Grid: A decentralized energy system using photovoltaic panels for electricity generation and battery banks for storage thus providing power to a defined community or facility at capacities typically ranging from one kilowatt to several hundred kilowatts.

Internet of Things (IoT): A connection of physical devices embedded with sensors, microcontrollers, and communication interfaces enabling autonomous collection and transmission of operational data to processing systems over a local or wide-area network.

Machine Learning (ML): A subset of Artificial Intelligence that enables algorithms to learn statistical patterns from training data and apply those patterns to generate predictions or decisions on previously unseen data without the need for explicit rule specification for each prediction scenario.

Anomaly Detection: The identification of rare data points, events, or observations that deviate significantly from the established normal behaviour distribution or simply the majority of data of a system, indicating a potential fault, degradation event, or irregular operations.

State of Health (SoH): A dimensionless metric which is expressed as a percentage to quantify a battery's current maximum charge storage capacity relative to its original factory-rated capacity. An SoH of 80% is mutually agreed on to be taken as the end-of-life threshold for most battery chemistry applications.

Remaining Useful Life (RUL): An estimate of the operating cycles or calendar time left before a component can no longer deliver performance thresholds like it used to.

Random Forest: An ensemble supervised learning algorithm that just creates multiple decision trees using bootstrap-aggregated training subsets known as bagging and random feature selection at each split and later on adding or combining all outputs by mean prediction (regression) or majority vote (classification) producing interpretable feature importance rankings.

Isolation Forest: An unsupervised algorithm that is used for anomaly detection that picks out outliers by isolating them using two key properties that they are few and are different thus instead of describing what normal data looks like it just picks out the outliers.

ESP32: A dual-core, 32-bit Xtensa LX6 system-on-chip microcontroller by Espressif Systems with integrated 2.4GHz Wi-Fi and Bluetooth. Active Wi-Fi power draw is approximately 160mA at 3.3V which means deep sleep current can fall to approximately 10 microamperes.

Store and Forward: A technique in telecommunication where a transmitting device locally buffers outgoing data when the channel is unavailable due to network connectivity issues and forwards the buffered data in batches once the connectivity is restored  and this preserves data integrity without requiring continuous network availability.

LittleFS: A fail-safe embedded file system by ARM mbed that uses  copy-on-write semantics that guarantee file-system integrity during power interruptions. LittleFS uses dynamic wear levelling and is the Espressif-recommended replacement for the deprecated SPIFFS which uses static wear leveling.

DS3231: A temperature-compensated crystal oscillator (TCXO) real-time clock module by Maxim Integrated that can be battery-backed with a CR2032 coin cell to maintain accurate absolute timekeeping while being independent of microcontroller power state.

Docker: A platform for building, shipping, and running applications in portable software containers and it handles all the tedious setup to an application like installing dependencies. A Docker image validated on a development laptop runs identically on any Docker-enabled host, including a Raspberry Pi 4 or cloud VPS without code modification (Docker Documentation, 2025).

Proof of Concept (PoC): A demonstration that a system being proposed is technically feasible. A PoC validates the architecture, the algorithm performance, and the system logic. The environment where the proof of concept was built does not place any restrictions on where the system can eventually be deployed in production

Sim-to-Real Gap: The difference between simulation-generated training data and data from real-world sensor measurements that arises from idealised models that omit sensor noise.

Concept Drift: A phenomenon in which the relationship between ML model input features and the target variable shifts over time as the physical system ages which causes the learned patterns and predictions of a static model inaccurate.

MQTT: A publish and subscribe messaging protocol designed for resource-constrained devices on unreliable networks. I used it with QoS 1 ('at least once') with persistent sessions that  guarantees message delivery to the broker when upon network restoration.

## 1.9 Chapter Summary

This chapter has introduced the operational and technical context for the research. Zimbabwe's electricity supply deficit has created an environment in which decentralised solar mini-grids are economically essential but still critically under-maintained, and the monitoring gap between the hardware that exists and the intelligent systems needed to protect it defines the specific problem this research addresses. The aim, five specific objectives, and the four-tier significance of the study have been stated. The economic analysis in Section 1.5.4 establishes that the total deployment cost which is approximately 1.5%–2.5% of the capital value of the most important component to be protected which is the battery asset which satisfies the rational investment standard for capital equipment protection. Key technical terms have been defined with engineering precision, establishing vocabulary used throughout Chapter 2. The following chapter shows a critical review of existing research on this, rigorously identifying the four specific technical and contextual gaps that justify every major architectural decision of the proposed system.

# CHAPTER 2: LITERATURE REVIEW AND RELATED WORK

## 2.0 Introduction

This chapter critically reviews existing research related to the design and implementation of a Machine Learning-based predictive maintenance system for decentralised solar mini-grids using IoT sensors, which is the specific focus of this project. The purpose of this review is to examine previously proposed solutions for solar PV fault detection and health monitoring, analyse their technical strengths and weaknesses, and identify the gaps that justify the need for the proposed system.

Recent advances in low-cost embedded computing and data-driven analytics have enabled a range of intelligent monitoring frameworks for solar energy systems. Despite all this measurable progress, some technical challenges remain unaddressed for example, in areas where there is intermittent connectivity achieving real-time anomaly detection becomes a challenge, battery’s State of Health prediction for small-scale off-grid deployments, and the absence of offline data preservation mechanisms in existing IoT-based architectures have been exploited but not enough in Southern Africa. Researchers have proposed approaches that bridge traditional rule-based threshold monitoring, supervised ensemble machine learning, deep learning architectures, IoT sensor frameworks, and edge computing paradigms. Each carrying a distinct profile of computational cost, data requirements, connectivity dependence, and deployment complexity that must be evaluated against the operational constraints of Southern Africa and Zimbabwe to be specific.

The chapter is structured as follows: Section 2.1 presents the theoretical background. Section 2.2 reviews existing approaches, organized in relation to the theme from traditional through intelligent to emerging methods. Section 2.3 provides a comparative study and analysis of existing systems using two structured tables. Section 2.4 identifies the research gap. Section 2.5 introduces the conceptual direction of the proposed solution.

## 2.1 Theoretical Background
Before diving into the review of existing approaches, this section lays out all the key concepts, technologies, and the real-world feasibilities or practicalities that are essential for understanding the research problem

### 2.1.1 PV Fault Taxonomy and Operational Dynamics

A solar PV mini-grid is made up of a few key components namely the photovoltaic panels, a Battery Energy Storage System (BESS), a charge controller, and an inverter for DC-to-AC conversion. In a comprehensive taxonomy of faults in grid-connected solar systems by Kull et al. (2025) that categorises PV faults into three technical classes, namely DC-side faults, including all open-circuit failures, short-circuit conditions, and bypass diode degradation, AC-side faults, which include all inverter thermal stress, MPPT controller failure, and grid synchronisation disturbances. Lastly, there is environmental degradation, this comprises of panel soiling, partial shading, and potential-induced degradation (PID) to mention only a few. We do this type of classification framework to structure both the synthetic dataset's fault injection scenarios and the anomaly detection evaluation criteria.

The driver of PV output is solar irradiance (W/m²). Higher irradiance increases photocurrent but at the same time raises cell temperature. The interaction between the two is non-linear, and silicon PV cells lose approximately 0.3%–0.5% of power output per degree Celsius above the Standard Test Condition baseline of 25°C. Ambient temperatures reach up to 38-42°C under Zimbabwean summer conditions and this may cause cell temperatures in direct sunlight to reach 55–70°C, implying real-world efficiency losses of 15–23% relative to rated output. This irradiance-temperature interaction must be modelled accurately in the training data to prevent the ML system from misclassifying thermally induced power reduction as a fault. in series-connected string configurations partial shading can cause a single shaded cell to act as a resistor rather than a generator, disproportionately reducing the entire-string output and creating hotspot conditions that accelerate cell degradation.

### 2.1.2 The Sub-Saharan African Operational Reality

In sub-Saharan Africa the operational failure modes of solar mini-grids are not simply theoretical but they have been empirically documented in real deployments. Mehta et al. (2025) conducted the first technical analysis of two officially recognized mini-grids in Namibia at Tsumkwe and Gam using six years of operational data collected from 2017 to 2022. The study identified battery overheating as the main driver of efficiency decline at the Tsumkwe mini-grid, resulting in significant capacity degradation over the period. The batteries in the Tsumkwe system had already degraded to a point where the mini-grid was experiencing a marked surge in diesel consumption to compensate for reduced storage capacity by 2022 which is an economic and operational result of not using active battery health monitoring. The Gam mini-grid which was initially oversized faced the inverse problem of increased demand outstripping its ageing storage capacity afterwards.

These findings constitutes to the empirical evidence in the literature for the present study since they confirm that battery thermal stress and degradation in the temperature conditions present in Zimbabwe can cause operational and economic failures that the proposed monitoring system is designed to prevent. The Tsumkwe and Gam case studies demonstrate that the problem is not hypothetical and that its results ended up increasing dependence on fossil fuel as backup, reduced solar energy reliability, and accelerated capital expenditure on battery replacement which is financially straining for the communities affected.

### 2.1.3 The Battery Energy Storage System as the Critical Failure Point

State of Charge (SoC) and State of Health (SoH) quantify Battery health, where SoH represents the battery's current capacity as a fraction of its original rated capacity which is 80% SoH is the acceptable end-of-life threshold. Electrical parameters the likes of terminal voltage, discharge current, and temperature are the ones used to measure SoH (Abdulla et al., 2024). Deep cycling, which is repeated discharge beyond the recommended Depth of Discharge threshold and elevated ambient temperatures that accelerate electrochemical degradation are the main causes of failure in the Zimbabwean context (Patabo et al., 2024).

A key measurement limitation must be acknowledged in cost-constrained field deployments where temperature is measured at the battery surface rather than internally. Raijmakers et al. (2022) confirmed that to measure non-invasive internal temperature, it requires embedded fibre-optic or electrochemical probe sensors which are not practical for field installation at small-scale cost points. Surface temperature measurement is the de facto standard in IoT-based battery monitoring. Random Forest ensemble methods can learn the statistical correlation between surface thermal dynamics and internal degradation trends with sufficient accuracy for SoH estimation purposes in field-deployed systems (Abdulla et al., 2024).

### 2.1.4 Machine Learning Fundamentals for Predictive Maintenance

Random Forest, introduced by Breiman (2001), is an ensemble supervised learning method constructing multiple decision trees using bootstrap-aggregated training subsets and random feature subsetting at each split node. For regression tasks such as SoH estimation, it outputs the mean prediction across all trees; for classification tasks, it outputs the majority class vote. The dual randomisation strategy reduces prediction variance, providing strong generalisation on high-dimensional, non-linear feature spaces without requiring feature normalisation. The algorithm produces interpretable feature importance rankings that identifies which parameters being monitored have strongly contributed to the prediction of the degradation, thus supporting informed maintenance prioritisation in cost-constrained field deployments.

Liu, Ting, and Zhou (2008) proposed the Isolation Forest which uses the structural isolation principle of anomalous observations which means looking for rare and geometrically distinct from the normal data cluster which are separated in fewer random partitioning steps than normal observations. The algorithm is entirely unsupervised which means it requires no labelled fault examples during training, and has linear time complexity of O(n). This makes it efficient for repeated CPU-based server-side inference. These two properties are architectural necessities for the present study where no historical fault records exist for model training.

### 2.1.5 The Five-Layer IoT Architecture for PV Monitoring

The canonical architectural framework for IoT systems relevant to solar PV monitoring is the five-layer model that comprises of the Perception layer (relying on microcontrollers and physical sensors to gather real-time electrical and environmental data), the Network layer (communication protocols transmitting data between devices and servers), the Middleware layer (data storage, processing pipelines, and service management functions), the Application layer (domain-specific user interfaces and visualisation dashboards), and the Business layer (analytics, alert logic, and integration with maintenance workflows) (Shukla et al., 2026; Al-Fuqaha et al., 2015). The Perception layer in the proposed system is implemented by the ESP32 microcontroller with its sensor array, the Network layer uses Wi-Fi with MQTT QoS 1 protocol, the Middleware layer comprises of the MySQL database and Python/FastAPI ML microservice and Nodejs for webservices, the Application layer is the React PWA dashboard, and the Business layer encompasses the automated alert notification engine and the model recalibration workflow. This  five-layer mapping provides a structured basis for evaluating and comparing with existing IoT monitoring implementations reviewed in Section 2.2.

### 2.1.6 The BH1750 Illuminance Sensor as a Validated Irradiance Proxy

The standard physical quantity for solar energy input is broadband irradiance in W/m² which is measured using a thermopile pyranometer costing several hundred dollars per unit. The BH1750 digital ambient light sensor measures illuminance in lux and it costs approximately two US dollars per unit. The BH1750 is sensitive only to visible wavelengths of approximately 400–700nm, whereas a silicon PV cell responds to the broader spectral range of approximately 350–1150nm including near-infrared energy. Michael, Johnston, and Moreno (2020) established that 1,000 W/m² corresponds to approximately 120,000 lux under outdoor sunlight which can be used as a nominal conversion factor of approximately 0.0083 W/m² per lux for clear-sky conditions.

Alcalá-Rodríguez et al. (2025) trained a Random Forest model to translate BH1750 lux readings to irradiance values measured in watts per square meter. They used a high-precision pyranometer as their reference, achieving R² = 0.9922, RMSE = 44.46 W/m², and MAE = 27.12 W/m². Topalović et al. (2024) demonstrated R² = 0.97894 for solar panel output voltage estimation using BH1750 illuminance as the main input feature. These results confirm that BH1750 illuminance is a highly informative and validated proxy feature for ML-based PV monitoring but under clear-sky conditions, which predominate in Zimbabwe's semi-arid climate (over 300 sunny days annually). The BH1750 selection reduces sensor cost by approximately 99% relative to a research-grade pyranometer which was supported by peer-reviewed experimental evidence.

### 2.1.7 The Resource-Constrained Deployment Context

For this deployment, the resource-constrained deployment is characterized by four properties which are intermittent internet connectivity (Patabo et al., 2024), hardware cost per monitoring node constrained well below industrial sensor network pricing, ESP32 hardware incapable of in-memory ML inference due to 520KB SRAM limitations, and the absence of historical fault data which led to simulated datasets. Each constraint rules out a number of architectural options that might look appealing otherwise, and it directly shapes the design decisions we will examine and assess in the sections that follows.

## 2.2 Review of Existing Approaches

This section reviews previous research conducted in the problem domain. The review is organised thematically by the evolution of technologies and methodologies used to address solar PV fault detection and health monitoring.

### 2.2.1 Traditional and Rule-Based Approaches

System fault detection and maintenance for PV solar mini-grids relied on manual inspection, reactive repair, and static electrical threshold comparisons at the early stages. These ways established foundational knowledge about the failure modes but were structurally not adequate to detect the complex, multi-parameter degradation signatures that enhance component failure.

Patabo et al. (2024) conducted a study of maintenance practices across household solar power plants in rural Indonesia, which is a deployment in the same context to rural Zimbabwe in system scale, operating environment, and technical support availability. Their results confirmed that battery degradation, inverter overloads, and panel soiling were the three main failure modes and that the available reactive maintenance models failed to detect any of them before real damage occurred. This empirical evidence from a deployment made in a developing-economy establishes the documented inadequacy of reactive approaches. Patabo et al. (2024) however did not propose automated monitoring solution and the paper is a diagnostic study that forms the baseline against which intelligent monitoring approaches are compared.

The first attempt to automate fault signalling without ML is the Static threshold-based monitoring. Nassar et al. (2024) developed and deployed an ESP32-based IoT monitoring device for PV systems at capacities up to 90 kW while transmitting data to the ThingSpeak cloud platform at two-minute intervals and triggering SMS alerts when inverter load exceeded 80W or battery voltage fell or rise above a fixed threshold. This work proves the ESP32 works well for PV data acquisition, however, two architectural absences are instructive. First, a fixed threshold of 80W cannot tell between a genuine fault condition and a legitimate heavy load happening. The same voltage reading could mean either one, depending on things like temperature, what time of day it is, and how long the system has been discharging which is the context that a simple scalar threshold simply cannot account for. Second, when network connectivity was disrupted during the deployment all sensor readings were permanently lost and timestamps were corrupted since the system did not have in use a local data buffer or a hardware real-time clock. These specific absences mentioned are what the LittleFS, Store and Forward mechanism and the DS3231 RTC in the proposed system responding to. These traditional ways provided important foundational knowledge but are fundamentally not capable of multi-parameter contextual analysis that is required for proactive fault detection.

### 2.2.2 Intelligent and Data-Driven Systems

The transition made from rule-based to data-driven monitoring shows that solar PV fault signatures are multi-parametric, non-linear, and context-dependent properties that threshold-based logic cannot capture but that machine learning is designed to exploit. Tasmant et al. (2025) emphasize that the integration of renewable energy sources into microgrids introduces severe challenges regarding generation variability and system reliability. Traditional fault detection ways cannot adapt to the irregular nature of these renewable sources, this makes the integration of machine learning so essential to achieve the required diagnostic accuracy.

Pillai, Devaraj, and Selvam (2025) conducted the most directly relevant ML benchmarking study for the present work. Using five years of real-time operational data from a 33kW grid-connected PV system, a dataset of 23,000 instances covering seven fault categories including inverter faults, MPPT controller failures, grid irregularity, and PV array mismatch, the study evaluated six supervised ML classifiers. Random Forest emerged as the dominant algorithm with a classification accuracy of 98.7% and a standard deviation of 0.003, substantially outperforming Decision Trees (lower accuracy), SVM (lower accuracy across all categories), KNN, Logistic Regression, and Naive Bayes. The hardware prototype used ESP32 (NodeMCU) microcontrollers with voltage, current, and temperature sensors. These results are the empirical basis for the Random Forest selection in the present study. A critical limitation must be stated: the system required continuous IFTTT server connectivity and was tested exclusively on a utility-scale grid-connected installation. Performance under intermittent connectivity with synthetic training data is not evaluated.

Kabir, Shufian, and Zishan (2023) evaluated the Isolation Forest algorithm for PV anomaly detection on a dataset of 45,740 operational observations, correctly identifying 453 anomalous data points, approximately 1% contamination consistent with a well-maintained system's expected fault rate, and attributed approximately six panel-level fault events from the flagged anomalies through a rule-based post-processing module. This provides empirical confirmation that the Isolation Forest performs effectively for PV anomaly detection without any labelled fault examples in the training set of data. The hardware context was not specified and the study did not address deployment or timestamp keeping during network outages.

Mellit, Benghanem, Kalogirou, and Massi Pavan (2023) developed an embedded system integrating ANN-based ML inference with IoT data acquisition on a Raspberry Pi single-board computer which achieved reliable multi-class fault classification. The power consumption comparison with the ESP32 is architecturally decisive for the target context because a Raspberry Pi 4 draws approximately 2–3W at idle which is like 500–600mA at 5V as a continuous parasitic load on the battery bank being monitored. The ESP32 draws approximately 160mA while on active Wi-Fi transmission and can go to sleep which reduces power drawn. In a standalone household-scale solar system where the monitoring hardware must be powered by the battery bank it monitors using a continuous 500mA drain represents a meaningful and persistent energy loss. Mellit et al. (2023) do not report power consumption figures or cost per node, yet these are the decisive engineering parameters for the target deployment in context.

Kull et al. (2025) made a comprehensive review of faults and predictive maintenance for grid-connected solar systems and confirmed that ensemble tree-based methods, particularly Random Forest and gradient boosting variants provide the best balance of accuracy and computational efficiency for multi-class fault detection. Deep learning architectures like CNNs and LSTM networks achieve comparable accuracy in research settings but require greater computational resources and training data volume. This makes them impractical for CPU-only edge deployment where resources are constrained. This finding supports both the algorithm selection and the server-side inference architecture of this study.

### 2.2.3 IoT-Based Monitoring Frameworks and Edge Computing

A large body of research examined the hardware and communication architectures for deploying monitoring systems on physical solar installations which includes the critical but often overlooked question of embedded file system resilience and communication protocol design.

Hamasha et al. (2025) developed an IoT-based predictive maintenance framework that shifted ML inference from a remote cloud server to edge hardware. This translates to 40% less downtime compared to downtime you would get processing everything in the cloud. The framework's edge architecture reduced the latency for alerts by eliminating round-trip delays to the remote servers. However, the hardware was considered more expensive than consumer-grade microcontrollers, and the authors acknowledged that full edge-intelligence deployment and running of trained models directly on constrained hardware remains not practical for low-budget deployments. This finding directly informed the hybrid architectural decision in this study which involves the ESP32 to handle data acquisition and LittleFS buffering, while the Random Forest and Isolation Forest inference runs on the server-side on a Docker-containerised FastAPI service. This shows the data integrity advantages of local buffering without the need of on-device ML inference capability.

The five-layer IoT architecture (Shukla et al., 2026) described in Section 2.1.5 provides the framework for us to understand why the communication protocol selection at the Network layer is an architectural decision rather than an implementation detail. MQTT's three Quality of Service (QoS) levels guarantees delivery across unreliable networks. QoS 0 provides no delivery confirmation this means messages lost in transit are permanently lost. QoS 1 ('at least once') guarantees delivery via broker acknowledgement and retransmission and is infused with persistent sessions queuing undelivered messages for offline clients on reconnection. The system developed by Nassar et al. (2024) did not include any QoS mechanism and this explains its data loss during connectivity failures. The proposed system implements MQTT QoS 1 with persistent sessions as the second tier of its data integrity architecture in addition to the LittleFS local buffer.

### 2.2.4 Emerging Technologies

Recent research has introduced two additional considerations relevant to the long-term operational validity of the proposed system: concept drift management and the choice of embedded file system for power-loss resilience.

Concept drift is the progressive shift in the statistical relationship between sensor features and the target variable as physical hardware ages and is confirmed by Vichare and Gaikwad (2025) across their review of 122 papers as an unaddressed challenge in deployed PV predictive maintenance systems. The operational consequence is concrete because a Random Forest SoH model trained when a LiFePO4 battery was new might learn that a resting terminal voltage of 13.2V corresponds to 90% SoC. After two years of deep cycling in Zimbabwe's summer temperatures the electrochemical aging may cause the same 13.2V reading to correspond to only 75% SoC. This shows that the model systematically overestimates available energy when used without recalibration which can potentially trigger deep-discharge events that accelerate the degradation it was designed to prevent. The proposed system addresses this by data logging from the first deployment and accumulating labelled time-series data that can later be used for periodic model recalibration. On the selection of embedded file system Espressif Systems formally deprecated SPIFFS (SPI Flash File System) due to its insufficient power-loss resilience. A write operation interrupted by a brownout can leave SPIFFS in a corrupted state that requires manual recovery which is not acceptable for an autonomous field device in a solar mini-grid that may experience sudden voltage drops (Espressif Systems, 2024). LittleFS uses copy-on-write semantics that ensures the file system can go to its last known good state after a power loss at any point during a write. LittleFS additionally adds dynamic wear levelling and is highly recommended by Espressif as the SPIFFS replacement for all embedded storage applications on ESP32 hardware (Espressif Systems, 2024).

## 2.3 Comparative Analysis of Existing Systems

Different research approaches present trade-offs that can only be evaluated systematically by mapping them against the specific deployment constraints of the target context. Table 2.1 compares existing systems across the dimensions most critical for a resource-constrained Zimbabwean deployment, with the proposed system included in the final row to make the convergence of required features, and the gap it fills is visually explicit.

Table 2.1: Comparison of Existing Solar PV Monitoring and Predictive Maintenance Systems

| Author(s) (Year) | Algorithm / Technology | Hardware Platform | Connectivity Required? | Offline Capable? | Battery SoH? | Key Limitation in Context |
| --- | --- | --- | --- | --- | --- | --- |
| Patabo et al. (2024) | Reactive maintenance; manual inspection | None (manual) | N/A | Yes (no digital system) | No | All faults identified post-failure; no anomaly detection |
| Nassar et al. (2024) | Static threshold monitoring | ESP32 + GSM | Yes — ThingSpeak cloud required | No — data lost on outage; no RTC | No | Fixed 80W threshold; no ML; data permanently lost during connectivity failures |
| Kabir et al. (2023) | Isolation Forest (unsupervised) | Unspecified | Unspecified | Unspecified | No | No hardware prototype; offline operation and RTC timestamping untested |
| Mellit et al. (2023) | Embedded ANN | Raspberry Pi 4 | Yes, server required | Partial | No | Raspberry Pi 4 draws ~2–3W idle; 500–600mA parasitic load on monitored battery bank; no SoH component |
| Pillai et al. (2025) | Random Forest: 98.7% accuracy, SD 0.003 (7 fault classes) | ESP32 (NodeMCU) | Yes, IFTTT/Google required continuously | No, no local buffer | No | 33kW utility-scale grid-connected; no evaluation under intermittent connectivity |
| Hamasha et al. (2025) | Edge computing + IoT framework | Industrial edge hardware | Intermittent (reduced dependency) | Partial | No | Hardware cost prohibitive for low-budget rural deployments; no battery SoH |
| Ahmed et al. (2025) | Systematic review (87 studies) | N/A (review only) | N/A | N/A | No | Review only; no validated off-grid implementation provided |
| This Study (Proposed) | Random Forest (SoH regression) + Isolation Forest (anomaly detection) | ESP32 + LittleFS + DS3231 [PoC: laptop; Production: cloud VPS or Pi 4 via Docker] | Intermittent, designed for it | Yes, LittleFS + DS3231 hybrid timekeeping | Yes | Synthetic training data with Gaussian noise injection; laboratory-scale PoC validation |

The trend that has been created by Table 2.1 is clear. Predictive systems of high strength and capability, Mellit et al. (2023), Pillai et al. (2025) which require either costly hardware or continuous cloud connectivity, and none of them has local data buffering with offline-resilient timestamping. Systems using affordable ESP32-class hardware such as Nassar et al. (2024) reach a state of only static threshold monitoring which permanently lose data when disconnected, and have no policy of maintaining correct timestamps in the event of network failures. No reviewed system simultaneously provides: affordable ESP32-class hardware, LittleFS offline buffering, DS3231 timestamp integrity, MQTT QoS 1 delivery guarantees, server-side ML inference, battery-specific SoH prediction, and a Docker-containerised deployment pathway from PoC to production.

Table 2.2 further breaks down the analysis to the specific ML algorithms tested in the reviewed literature, comparing them to proven performance statistics and the implementation limitations of this study.

Table 2.2: Comparison of Machine Learning Algorithms used to detect Solar PV Faults and Health Prediction

| Algorithm | Type | Diagnostic Accuracy (Verified) | Computational Complexity | Offline Inference? | Suitability — This Study |
| --- | --- | --- | --- | --- | --- |
| Random Forest | Supervised ensemble | 98.7% accuracy, SD 0.003, 7 fault categories (Pillai et al., 2025); R² = 0.97894 panel output from BH1750 (Topalović et al., 2024) | Low–moderate; no GPU; CPU-only | Yes, runs on laptop/Pi 4/VPS via Docker | HIGH, best verified accuracy; interpretable; noise-robust; platform-agnostic |
| Isolation Forest | Unsupervised | 453 anomalies isolated from 45,740 PV observations (Kabir et al., 2023) | Very low; linear O(n) | Yes, CPU-only | HIGH, no labelled fault data required; computationally efficient; essential given no historical fault records |
| SVM | Supervised | Lower than RF across all 7 fault categories in direct benchmarking (Pillai et al., 2025) | Moderate; sensitive to kernel selection and feature scaling | Yes | MODERATE, inferior accuracy to RF; harder to tune and maintain in field |
| LSTM / CNN | Deep learning | High accuracy in research settings; performance figures vary with dataset | Very high; GPU typically required; large labelled dataset required | No, requires cloud GPU for inference at scale | LOW, GPU and stable connectivity required; impractical for rural Zimbabwe deployment |
| XGBoost | Supervised ensemble | R² up to 0.9998 on NASA EV battery benchmark datasets | Moderate–high; complex hyperparameter tuning required | Yes | MODERATE, marginal accuracy gain over RF for SoH; less interpretable; harder to recalibrate without ML expertise |
| ANN | Supervised neural | Over 95% classification accuracy on ANN-based PV system (Mellit et al., 2023) | Moderate–high; training dataset size sensitive | Yes | MODERATE, comparable accuracy but requires substantially larger training datasets than RF ensemble |

Table 2.2 confirms the algorithm selection rationale. Random Forest offers 98.7 percent accuracy (SD = 0.003) on real world operational data of the domain (Pillai et al., 2025), no GPU needed, and produces interpretable outputs. Its R² = 0.97894 when used with BH1750 illuminance for panel output estimation (Topalović et al., 2024) validates the illuminance-as-proxy design choice. Isolation Forest requires no labelled fault history and has O(n) complexity, architectural requirements due to the lack of history of faults. Deep learning methods(LSTM, CNN) can technically be eliminated but are not, not because they do not work perfect in this case but because of the deployment feasibility consideration: their GPU requirements, big labelled dataset dependencies, and the fact that the system must be connected to cloud all the time are incompatible with the target deployment context, as confirmed by Kull et al. (2025). This comparison reveals the need for systems that offer a balance between accuracy, offline capability, and cost-effectiveness to the specific case of decentralised mini-grids.

## 2.4 Research Gap

Although there has been major advancements in systems that aim at dealing with solar PV fault detection the analysis of existing literature shows that four specific and distinct are identified in health monitoring limitations which are collective in the research contribution of the proposed system. These are not vague claims of narrow coverage but they are specific architectural and contextual laws that can be identified based on the evidence that is reviewed in this chapter.

Most existing IoT monitoring systems using affordable ESP32-class hardware such as Nassar et al. (2024) consistently lack both local data buffering and offline timekeeping, causing permanent data loss and epoch-timestamp corruption during connectivity failures. Simultaneously, ML-based fault detection systems such as Pillai et al. (2025) and Mellit et al. (2023) assume continuous cloud connectivity and are never evaluated under intermittent-connectivity conditions. No validated architecture in the reviewed literature bridges this divide: combining low-cost ESP32 hardware, LittleFS-based Store and Forward buffering, DS3231 hardware RTC for timestamp integrity, MQTT QoS 1 delivery guarantees, and server-side ML inference, all integrated and designed specifically for intermittent-connectivity operation.

Additionally, ML-based battery SoH prediction research is conducted almost exclusively using EV battery test bench datasets, primarily the NASA battery dataset with cycling profiles and temperature ranges that differ materially from the small-scale lead-acid and LiFePO4 batteries operated in Zimbabwean households under summer ambient temperatures of 38–42°C. The Tsumkwe mini-grid case study (Mehta et al., 2025) confirms that battery overheating under exactly these conditions is a real and documented cause of system failure in sub-Saharan African mini-grids, yet no reviewed study validates SoH prediction methods for this specific operational context. Furthermore, no reviewed ML-based PV monitoring study injects sensor-specific Gaussian noise into simulated training data to bridge the sim-to-real gap leaving models potentially overfit to idealised data and vulnerable to real sensor noise from the ACS712's documented 1.5% total output error and temperature-dependent quiescent drift (Allegro MicroSystems, 2024).

As Vichare and Gaikwad (2025) confirm across 122 reviewed papers, no published PV predictive maintenance architecture describes a system designed for periodic model recalibration against accumulated in-field operational data. Every reviewed system treats model deployment as terminal, implicitly assuming that the statistical relationship between sensor readings and component health remains constant over the deployment lifetime which is an assumption that is physically incorrect for systems subject to progressive electrochemical degradation and panel UV aging. Finally, as Marangis et al. (2025) found, with 93% of PV maintenance papers addressing corrective rather than predictive approaches and the predictive minority focused almost exclusively on large installations above 100 kWp and no empirical study has validated a predictive maintenance system under the compounding conditions of sub-Saharan African decentralised mini-grids: high ambient temperatures, intermittent connectivity, consumer-grade sensors, synthetic training data, and end-users without proximate technical support. Therefore, there is a clear need for a system that: combines offline data integrity with ML-based predictive capability; validates battery SoH prediction under high-temperature, small-scale deployment conditions; manages model concept drift through continuous operational data logging; and provides empirical validation under the specific conditions of the Zimbabwean decentralised mini-grid context. Addressing these gaps forms the main motivation for the present research.

## 2.5 Proposed Conceptual Solution

This study suggests the development of the system based on the limitations found in the literature which are a low-cost, offline-enabled predictive maintenance system for decentralized solar mini-grids that bridges the gap between academic algorithmic innovation and practical deployability in resource-constrained environments.

The proposed system incorporates the ESP32 microcontroller programmed using LittleFS-based Store and Forward firmware that enables buffering data in case of network failures, a DS3231 TCXO RTC to handle properly the offline timestamps without network connectivity to NTP, MQTT QoS 1 with persistent sessions for guaranteed delivery on the server-side upon reconnection, a Python/FastAPI ML microservice running Random Forest regression to estimate the battery’s SoH and Isolation Forest to detect anomalies without supervision, and both models are stored in memory so that we can achieve millisecond per-prediction latency, a high-concurrency telemetry ingestion Node.js/Express server and no blocking ML inference, and a React Progressive Web App dashboard to real-time visualization and automated alert notifications. The entire server stack is containerized in Docker which enables the system to be run on a development laptop to validate PoC and on a Raspberry Pi 4 (official price: $35) or cloud VPS for production, without any changes to application code (Docker Documentation, 2025; Hashim et al., 2025).

More importantly, the training dataset is generated by a simulation engine that injects sensor-specific Gaussian noise randomized to hardware datasheets, ±1.5% on current readings (ACS712), ±0.5% on power and voltage (PZEM-004T), ±2 lux on illuminance (BH1750), to avoid model overfitting to unrealistically clean simulation data. The ACS712's temperature-dependent quiescent voltage drift is another issue which is mitigated by auto-zero calibration on firmware level. The system is developed as a continuous operation data logger in the place and starts logging on deployment day. This enables periodic recalibration of the models as the hardware being monitored ages directly and this addresses the concept drift gap found in Vichare and Gaikwad (2025). The expected benefits of the suggested system are: enhanced battery life due to early identification of abusive discharge patterns; less operational downtime occurring due to predictive fault alerting; offline data integrity through the three-layer LittleFS/DS3231/MQTT architecture; and a total hardware cost of approximately $25–$30 per ESP32 node that represents 1.5%–2.5% of the capital value of the battery asset being protected which is the main costy component. The specifications of the hardware, firmware architecture, software design, and implementation methodology are presented in Chapter 3.

## 2.6 Chapter Summary

In this chapter, the review of existing literature concerning Machine Learning-based predictive maintenance for decentralised solar mini-grids was conducted, research of traditional rule-based methods, smart ML-related fault detection systems, IoT monitoring frameworks, and new technology such as concept drift management and embedded file system resilience. The strengths and limitations of these methods were compared against the specific operational constraints of Zimbabwean decentralised mini-grid installations with a quantified evidence provided throughout: 98.7 percent Random Forest accuracy (SD = 0.003) on real operational data; BH1750 R² = 0.9922 for irradiance estimation via ML conversion; Raspberry Pi 4 idle consumption of 2–3W versus ESP32's 160mA active draw; ACS712 total output error of 1.5% at 25°C with thermal drift recorded; and LittleFS's copy-on-write power-loss resilience as per Espressif official documentation. According to this analysis, four research gaps were identified namely: the architectural disconnection between intelligence and offline capability; the discrepancy between simulation and reality in training data; the absence of concept drift control; and the absence of contextual validation of the deployment conditions in sub-Saharan Africa was validated by real-world evidence from the Tsumkwe and Gam mini-grids in Namibia (Mehta et al., 2025). The next chapter presents the research methodology and system design through which these gaps are addressed in a working prototype.

# CHAPTER 3: RESEARCH METHODOLOGY AND SYSTEM DESIGN

## 3.0 Introduction

This chapter details the methodological framework and system design used to construct the predictive maintenance prototype. Taking the four research gaps identified in Chapter 2 as its starting point, this chapter explains how the proposed solution was put into operation, what hardware was selected and why, how the software architecture was structured, how the machine learning pipeline was built, and how the system will be evaluated to confirm that it performs as claimed.

The chapter addresses five questions that any rigorous engineering methodology must answer: what research approach was used; how the system was developed; what tools were used; what data the system uses and how it was collected; and how the system is evaluated. Each is addressed in turn across the following ten sections.

The chapter is organised as follows: Section 3.1 explains the research design. Section 3.2 describes the research methods applied. Section 3.3 presents the system architecture. Section 3.4 describes data collection methods. Section 3.5 lists the tools and technologies used. Section 3.6 details the system implementation phases. Section 3.7 describes system testing and evaluation. Section 3.8 addresses ethical considerations. Section 3.9 discusses the limitations of the methodology. Section 3.10 provides the chapter summary.

## 3.1 Research Design

This study uses a Design Science Research (DSR) methodology integrated with quantitative experimental prototyping. DSR is the standard methodology for computing and information systems research that produces knowledge through the act of building and evaluating a technological artefact (Hevner et al., 2004). In DSR, the designed artefact is not merely the output of the research but it is rather the main mechanism through which the research problem is investigated. This makes DSR appropriate for a project whose central objective is a functional predictive maintenance prototype.

Hevner et al. (2004) identify six stages in the DSR process: problem identification, definition of objectives, design and development, demonstration, evaluation, and communication of results. Table 3.1 maps each stage to the corresponding activities and deliverables of this study.

Table 3.1: Design Science Research Stage Mapping

| DSR Stage (Hevner et al., 2004) | Activity in This Research | Deliverable |
| --- | --- | --- |
| Stage 1: Problem Identification | Review of 122 existing PdM studies (Vichare & Gaikwad, 2025); analysis of solar mini-grid failure modes in sub-Saharan Africa (Mehta et al., 2025; Patabo et al., 2024); identification of four specific architectural and contextual gaps | Documented research gap (Chapter 2, Section 2.4) |
| Stage 2: Define Objectives | Specification of five measurable objectives covering offline data integrity, battery SoH prediction, anomaly detection, Docker-containerised deployment, and metric-based evaluation (Chapter 1, Section 1.4.2) | Five specific research objectives |
| Stage 3: Design and Development | Parametric simulation engine with Gaussian noise injection; ESP32 LittleFS + DS3231 firmware; Random Forest and Isolation Forest ML pipeline; Node.js + FastAPI + MySQL + React PWA backend stack | Working prototype system (Sections 3.6.1 – 3.6.4) |
| Stage 4: Demonstration | Laboratory end-to-end pipeline: sensor readings → ESP32 → MQTT → Node.js → FastAPI → React dashboard; five physical fault injection scenarios; 4-hour Store and Forward network outage simulation | System demonstration (Section 3.7.3) |
| Stage 5: Evaluation | RMSE, MAE, Precision, Recall, F1-score (ML metrics); Packet Delivery Ratio, end-to-end latency (engineering metrics); comparison against static-threshold baseline (Nassar et al., 2024) | Quantitative evaluation results (Chapter 4) |
| Stage 6: Communication | Formal undergraduate engineering thesis submitted to Department of ICT and Electronics, Chinhoyi University of Technology, in partial fulfilment of B.Eng. Honours in Computer Engineering | This thesis document |

The DSR framework is supported by two approaches that work hand in hand. Computer simulation addresses the absence of long-term historical fault data for local mini-grids: a Python-based parametric simulation engine generates the training dataset, with sensor-specific Gaussian noise injected to prevent overfitting. Experimental prototyping governs the physical hardware evaluation: the full edge-to-dashboard pipeline is assembled and tested in a controlled laboratory environment, with fault injection scenarios replicating the failure modes documented by Kull et al. (2025) and Patabo et al. (2024). The data problem is handled by simulation and empirical hardware testing handles the system validation problem. Both are necessary because neither is sufficient alone.

## 3.2 Research Methods

### 3.2.1 Design Science and System Design and Implementation

The main method is system design and implementation. This method involves translating identified research gaps into a functional computing artefact through iterative cycles of design, construction, testing, and refinement (Hevner et al., 2004). To qualify as a DSR contribution, the artefact must introduce an innovation not previously demonstrated. The specific innovation in this study is the integration of firmware-level offline timestamp preservation via DS3231 RTC, sensor-noise-calibrated simulation for training, Docker-containerised server-side ML inference, and field-validated BH1750 illuminance as an irradiance proxy, all targeting sub-Saharan African decentralised mini-grid deployments and it satisfies this criterion, as confirmed by the gap analysis in Chapter 2.

### 3.2.2 Empirical and Experimental Method

The experimental method governs the evaluation phase. Controlled experiments are designed to answer five measurable questions that is does the Random Forest SoH model achieve RMSE below 5% SoH units on the held-out test partition? Does the Isolation Forest detect all five injected fault scenarios? Does the Store and Forward mechanism achieve 100% Packet Delivery Ratio during a 4-hour simulated network outage? Does the system achieve end-to-end alert latency below 30 seconds? Does ML-based detection outperform static-threshold monitoring on the same fault injection dataset? These questions produce quantitative, reproducible answers, which is the standard that distinguishes an engineering evaluation from a demonstration.

### 3.2.3 Computer Simulation Method

The computer simulation method addresses the scarcity of long-term historical fault data for local solar mini-grids that is the data constraint identified in Chapter 2, Section 2.4. A Python-based parametric simulation engine generates a 30-day synthetic operational dataset for a 5kW standalone mini-grid. The simulation models diurnal irradiance profiles using sinusoidal approximations of solar elevation, temperature-dependent battery voltage-capacity relationships drawn from published lead-acid and LiFePO4 discharge curves, and inverter efficiency de-rating under varying load and thermal conditions.

The critical engineering intervention is sensor-specific Gaussian noise injection. Current readings receive ±1.5% noise (ACS712 total output error at 25°C per Allegro MicroSystems, 2024). Voltage and power readings receive ±0.5% noise (PZEM-004T measurement accuracy per PEACEFAIR, 2023). Illuminance readings receive ±2 lux noise (BH1750 typical accuracy). This prevents the models from overfitting to idealised data which is a failure mode identified in Section 2.4 that no reviewed study addresses. Without this intervention, models trained on simulation data would learn feature relationships that do not hold on real sensor hardware because firmware-level auto-zero calibration eliminates systematic thermal drift in the ACS712, the residual sensor error is modelled purely as Gaussian noise.

### 3.2.4 Artificial Intelligence Method

The AI method governs the selection, training, and deployment of the predictive intelligence layer. Two algorithms are applied and are selected on the basis of the comparative analysis in Chapter 2. Random Forest regression estimates the battery’s State of Health. The algorithm constructs 200 decision trees using bootstrap-aggregated training subsets (bagging) with random feature subsetting producing output for each tree and aggregating these results (mean) thus robust SoH prediction. Training uses a stratified 70/30 train/test split with five-fold cross-validation on the training partition to optimise estimator count and tree depth. Feature importance rankings are extracted post-training to confirm that battery terminal voltage, ambient temperature, and discharge current are the dominant predictors of SoH in addition the electrochemical mechanisms of battery degradation.

Isolation Forest is applied for multivariate anomaly detection. The algorithm is trained exclusively on the normal operation class of the simulation dataset, with a contamination parameter of 0.01 reflecting the approximately 1% anomaly rate documented by Kabir et al. (2023). Both trained models are serialised using joblib and loaded into memory at FastAPI microservice startup. This in-memory loading strategy reduces inference latency to under 50 milliseconds per prediction without any disk access on incoming telemetry records. The selection of these two lightweight ensemble models over deep learning architectures was justified on computational grounds in Chapter 2: CNNs and LSTM autoencoders require GPU acceleration and large labelled datasets, which are incompatible with the target deployment environment (Vichare & Gaikwad, 2025; Kull et al., 2025).

## 3.3 System Architecture

The proposed system is structured according to the five-layer IoT architectural framework described by Shukla et al. (2026), which organises IoT systems into the Perception, Network, Middleware, Application, and Business layers. This layered structure ensures that the edge data acquisition node, the ML inference engine, and the user visualisation layer can evolve, scale, and be maintained independently. Figure 3.1 presents the five-layer architecture.

Figure 3.1: Five-Layer IoT System Architecture

Source: Developed by the author, based on Shukla et al. (2026) five-layer IoT framework

### 3.3.1 Perception Layer (Edge Data Acquisition Node)

The Perception layer is implemented by the ESP32 microcontroller and its attached sensor array. The ESP32 was selected on power consumption grounds as it draws approximately 160mA during active Wi-Fi transmission compared with the Raspberry Pi 4's idle consumption of approximately 500–600mA at 5V (Raspberry Pi Ltd., 2025). In a standalone solar mini-grid powered by the battery bank being monitored, a continuous 500mA parasitic load is a design flaw. The ESP32 additionally supports deep sleep at approximately 10 microamperes between logging intervals, reducing average draw to under 50mA at a five-minute cycle.

The DS3231 TCXO RTC module is integrated via I2C to address the offline timestamp problem. The ESP32's internal clock resets to epoch time (1 January 1970) on power loss without NTP access (Last Minute Engineers, 2024). Every record written to LittleFS during an outage would carry a corrupt timestamp, destroying the chronological integrity of the time-series ML features. The DS3231 solves this by utilizing its coin-cell-backed oscillator which maintains accurate absolute time at ±2ppm independent of the ESP32's power state. On each boot, the firmware reads the DS3231 timestamp rather than defaulting to epoch. When NTP synchronisation is subsequently achieved, the firmware updates the DS3231 to NTP time for drift correction. Critically, the CR2032 backup cell is not intended to address routine network outages that happen during which the LM2596 buck converter continues supplying regulated 5V to the ESP32 from the battery bank but rather to preserve timekeeping through catastrophic power interruptions like a Battery Management System severing the circuit to protect cells from over-discharge, or an operator physically disconnecting the battery bank for maintenance, both of which cut the ESP32's supply voltage entirely.

### 3.3.2 Network Layer (MQTT Protocol with Store and Forward)

The Network layer uses MQTT with QoS 1 ('at least once') and persistent sessions. QoS 1 requires broker acknowledgement and retransmits unacknowledged messages, ensuring no telemetry record is lost due to a transient network failure. Persistent sessions cause the MQTT broker to queue messages published during a client's offline period and deliver them in order on reconnection.

When the MQTT connection fails, the firmware writes the current telemetry JSON to LittleFS. LittleFS was selected over SPIFFS because its copy-on-write semantics guarantee file-system integrity during power interruption like if voltage drops mid-write, the file system falls back to its last known good state (Espressif Systems, 2024). SPIFFS does not provide this guarantee and has been formally deprecated by Espressif. When Wi-Fi is restored, the firmware reads the LittleFS buffer sequentially and retransmits each record via MQTT QoS 1 before resuming real-time logging. Figure 3.2 presents the ML data pipeline, Figure 3.3 shows the flow diagram for the hardware connection and Figure 3.4 presents the firmware state machine for Store and Forward.

Figure 3.2: Machine Learning Data Pipeline Flowchart

Figure 3.3: Hardware Connection Block Diagram

Figure 3.4: ESP32 Store and Forward Firmware State Machine

### 3.3.3 Middleware Layer (Docker-Containerised Backend)

The Middleware layer comprises three Docker-containerised services orchestrated by Docker Compose that is the Node.js/Express telemetry ingestion service, the Python/FastAPI ML microservice, and the MySQL 8.0 database. Docker containerisation was selected to address the PoC-to-production deployment gap identified in Chapter 2 since a Docker Compose configuration validated on the development laptop deploys without code modification on a Raspberry Pi 4 or cloud VPS, confirmed by both Docker's multi-platform build documentation (Docker Documentation, 2025) and a peer-reviewed Scientific Reports study validating this exact architecture on Raspberry Pi 4 with FastAPI and Docker (Hashim et al., 2025).

The separation between Node.js and Python/FastAPI is architecturally necessary. Node.js's single-threaded and non-blocking event loop handles concurrent I/O efficiently with simultaneous MQTT-forwarded POST requests, MySQL writes, and WebSocket broadcasts, at approximately 40–60% higher throughput than Python for I/O-bound workloads (DEV Community, 2025). CPU-bound operations such as loading a 200-tree Random Forest into memory and running inference block Node.js's event loop, increasing telemetry ingestion latency. The FastAPI service keeps both models loaded in memory via joblib, serving inference requests asynchronously without affecting Node.js throughput. The MySQL schema is structured across four tables as telemetry, inference_results, alerts, and calibration_log. The calibration_log table is the specific mechanism that addresses the concept drift gap since it records RMSE and timestamp for each model recalibration event, enabling the operator to track model accuracy degradation over the deployment lifetime. To prevent UI thread saturation during a Store-and-Forward burst flush, the Node.js service inspects the record_source field on each incoming MQTT message, records flagged as store_and_forward are accumulated in memory and dispatched to the React client as a single batched WebSocket payload once the flush sequence completes, rather than as 48 individual events that would trigger 48 sequential chart re-renders in one second.

### 3.3.4 Application and Business Layers

The Application layer is a React.js Progressive Web App with a Service Worker configured to cache interface assets locally. The Service Worker caches the application shell and interface assets, allowing the dashboard UI to load and queue user commands during transient network drops that is to clear that live and historical data views require an active connection to the Dockerised backend. The dashboard implements five views: real-time sensor parameter charts with one-hour rolling windows that is a battery SoH gauge with green (>90%), amber (80–90%), and red (<80%) degradation zones, an anomaly alert feed listing the twenty most recent Isolation Forest detections with fault category labels and timestamp, a Store and Forward status indicator showing LittleFS buffer depth and last successful flush timestamp, and a model health panel displaying current RMSE and days elapsed since last recalibration.

The Business layer implements the alert notification engine and the model recalibration workflow. The alert engine evaluates each FastAPI inference result against two threshold rules that is SoH below 80% triggers a battery health alert and anomaly score above the contamination threshold triggers a fault detection alert. Alert records are persisted to the MySQL alerts table creating a detailed maintenance audit trail. The recalibration trigger on the dashboard initiates an automated retraining pipeline, the FastAPI service reloads all MySQL operational data accumulated since the last calibration, retrains both models on the combined simulation-plus-field dataset, serialises the updated models, and replaces the in-memory instances without service interruption. This workflow directly addresses the concept drift gap confirmed by Vichare and Gaikwad (2025) across 122 reviewed papers.

## 3.4 Data Collection Methods

### 3.4.1 Literature Review

Relevant academic literature was reviewed in Chapter 2 to identify existing technologies, algorithms, and systems related to the research problem. Databases consulted included IEEE Xplore, ScienceDirect, SpringerLink, MDPI, Google Scholar, and the ACM Digital Library. Search terms included predictive maintenance solar PV, IoT ESP32 solar monitoring, Random Forest fault detection photovoltaic, Isolation Forest anomaly detection, battery state of health machine learning, and LittleFS ESP32 offline storage. Inclusion criteria required publication between 2019 and 2026 with peer-reviewed journal or conference status. The review covered 122 existing PdM studies in the domain (Vichare & Gaikwad, 2025) and yielded the four specific research gaps motivating this system design.

### 3.4.2 Simulation Dataset Generation

The main data source for ML model training is the synthetic operational dataset generated by the Python simulation engine. The dataset represents 30 days of five-minute-interval telemetry for a 5kW standalone mini-grid with two 12V 200Ah lead-acid batteries in series and a 3kW pure-sine inverter. Eight features are generated per record that is solar irradiance proxy (BH1750 lux, converted to W/m² using 0.0083 factor per Michael et al., 2020), PV array output voltage (V), PV output current (A), battery terminal voltage (V), battery charge/discharge current (A), inverter output power (W), ambient temperature (°C), and a derived State of Health label (% capacity). Fault conditions are injected into 15% of records across the five fault classes drawn from the Kull et al. (2025) taxonomy, partial shading, battery deep discharge, inverter overload, MPPT failure, and sensor open circuit.

Sensor-specific Gaussian noise is applied post-generation using NumPy's random.normal function that is a standard deviation of 1.5% of mean current on ACS712 channels, 0.5% of mean voltage and power on PZEM-004T channels, and 2 lux on BH1750 illuminance. The processed dataset is split 70/30 into training and test partitions using scikit-learn's train_test_split. To preserve the 15% fault injection ratio across both partitions, the split is stratified based on the categorical fault class labels rather than the continuous SoH target variable

3.4.3 Physical Sensor Data Acquisition

Real sensor data is acquired during hardware testing via the ESP32 node operating on a physical test circuit. The test circuit comprises two 12V 7Ah sealed lead-acid batteries in series, a 150W pure-sine inverter, a 30W PV panel, and a 40W resistive load bank. Sensor readings are collected at five-minute intervals, transmitted via MQTT to the Node.js backend, persisted to MySQL, and compared against simulation predictions. Physical acquisition data serves two purposes, it verifies real sensor readings from the PZEM-004T, ACS712, BH1750, and DS18B20 fall within the noise envelope assumed during simulation, and it provides the early-stage operational baseline for concept drift monitoring. The DS18B20 probe is physically wedged between the two battery casings at the inter-cell contact face, the point of lowest heat dissipation and highest thermal stress in a series bank, and secured with thermal adhesive tape to ensure consistent surface contact across the evaluation period.

### 3.4.4 System Requirements Gathering

System requirements were derived from three sources. Technical requirements were extracted from the five research objectives in Chapter 1. Deployment context requirements were drawn from the literature review, specifically the operational conditions of rural Zimbabwean and sub-Saharan African mini-grids documented by Patabo et al. (2024), Mehta et al. (2025), and Madziyauswa (2024). Hardware specification requirements were drawn from the datasheets of the selected sensors, confirming that the ACS712 ±1.5% error, PZEM-004T ±0.5% accuracy, and BH1750 ±2 lux accuracy were within acceptable bounds for ML-based fault detection at this prototype's scale.

## 3.5 Tools and Technologies

### 3.5.1 Hardware Components

Table 3.2 lists all hardware components used in the edge acquisition node, with key specifications, approximate unit costs, and engineering justification for each selection. Total approximate hardware cost for a single ESP32 sensor node is $18–$27 which is within the $25–$30 per-node target established in the economic analysis in Chapter 1, Section 1.5.4.

Table 3.2: Hardware Components, Specifications, and Selection Justification

| Component | Interface | Key Specification | Cost (USD) | Engineering Justification |
| --- | --- | --- | --- | --- |
| ESP32 WROOM-32 (Espressif) | Wi-Fi, I2C, UART, ADC, 1-Wire | Dual-core 240MHz; 520KB SRAM; 4MB flash; 160mA active Wi-Fi; 10μA deep sleep | ~$4–6 | Active draw 94% lower than Raspberry Pi 4 idle (500–600mA); validated for PV sensor fusion and telemetry (Pillai et al., 2025) |
| DS3231 RTC Module (Maxim) | I2C (GPIO 21/22) | TCXO oscillator; ±2ppm accuracy; CR2032 coin cell backup; 0–70°C range | ~$1–2 | Prevents epoch-timestamp corruption on ESP32 reboot without NTP. Maintains ±2 seconds/day accuracy across multi-day outages (PCB Artists, 2024) |
| PZEM-004T v3.0 (PEACEFAIR) | UART (GPIO 16/17) | ±0.5% measurement accuracy; galvanic isolation; 80–260V AC; 0–100A; energy accumulation register | ~$6–8 | Galvanic isolation protects ESP32 3.3V logic from AC transients. Documented ±0.5% accuracy directly informs voltage and power channel noise injection parameters (PEACEFAIR, 2023) |
| ACS712-30A (Allegro) | ADC (GPIO 34) | ±1.5% total output error at 25°C; 100mV/A sensitivity; 2.1kVRMS isolation; quiescent drift over temperature | ~$1–2 | Hall-effect isolation; affordable; temperature-dependent drift addressed by firmware auto-zero calibration. Ambient temperature fed as ML feature for residual compensation (Allegro MicroSystems, 2024) |
| BH1750 FVI (ROHM) | I2C (GPIO 21/22) | 16-bit resolution; 1–65,535 lux range; ±2 lux typical accuracy; no external ADC required | ~$1–2 | Random Forest trained on BH1750 lux achieves R²=0.9922 for irradiance estimation vs. calibrated pyranometer (Alcalá-Rodríguez et al., 2025); 99% cost reduction vs. research-grade pyranometer |
| DS18B20 Waterproof Probe | 1-Wire (GPIO 4) | ±0.5°C accuracy over 0–70°C; stainless steel probe; parasitic power capable | ~$1–2 | Waterproof probe for battery casing surface attachment. Surface measurement is standard in cost-constrained field deployments (Raijmakers et al., 2022) |
| Breadboard + Jumper Wires + CR2032 | — | 830-point breadboard; 40-piece jumper wire set; CR2032 3V coin cell for DS3231 backup | ~$3–5 | Prototype-phase assembly. Production would migrate to custom PCB for environmental resilience |

### 3.5.2 Software Tools and Frameworks

Table 3.3 lists all software tools and frameworks used in the system with their specific roles in the architecture. All listed tools are open-source or have freely available developer licenses, contributing to the low-cost objective of the proposed system.

Table 3.3: Software Tools, Versions, and Architectural Roles

| Tool / Framework | Category | Version | Role in System Architecture |
| --- | --- | --- | --- |
| Python 3.11 | Primary language (server-side) | 3.11.x | Simulation engine; ML model training (scikit-learn); FastAPI ML microservice |
| scikit-learn | ML library | 1.4.x | RandomForestRegressor (n_estimators=200) and IsolationForest (contamination=0.01); model serialisation via joblib |
| Pandas + NumPy | Data processing | 2.x / 1.26.x | Simulation dataset construction; Gaussian noise injection (np.random.normal); feature engineering; stratified 70/30 train/test split |
| FastAPI + Uvicorn (ASGI) | ML microservice framework | 0.110.x | Exposes /predict endpoint; keeps RF and IF models in memory at startup (joblib.load); millisecond inference latency per record without disk I/O |
| Node.js 20 LTS + Express 4 | Telemetry ingestion backend | 20.x / 4.x | Event-driven MQTT subscriber; concurrent REST API; WebSocket broadcast to React dashboard; MySQL write operations. 40–60% faster than Python for I/O-bound concurrency (DEV Community, 2025) |
| MySQL 8.0 | Relational database | 8.0.x | Four-table schema: telemetry, inference_results, alerts, calibration_log. Provides the persistent operational dataset for concept drift recalibration (Vichare & Gaikwad, 2025) |
| React.js 18 + Vite 5 | Frontend PWA | 18.x / 5.x | Five dashboard views: sensor parameter charts, SoH gauge, anomaly alert feed, Store & Forward status panel, model health/recalibration panel. Service Worker enables offline historical data access |
| Arduino IDE 2 / PlatformIO 6 | Embedded firmware IDE | 2.x / 6.x | ESP32 C++ firmware development; LittleFS configuration; DS3231 RTC-Wire library; PZEM-004T UART driver; ACS712 ADC averaging |
| Docker 26 + Docker Compose 2 | Containerisation | 26.x / 2.x | Three-service Compose file: node_api, fastapi_ml, mysql_db on shared bridge network. Enables laptop → Pi 4 → cloud VPS deployment with zero code changes (Docker Documentation, 2025; Hashim et al., 2025) |
| EMQX / Mosquitto MQTT Broker | Message broker | 5.x / 2.x | QoS 1 + persistent sessions: queues undelivered messages for offline ESP32 clients; flushes queued batch on reconnection — second tier of data integrity architecture |
| Nginx | Reverse proxy / static server | 1.25.x | Serves built React PWA as static files inside Docker Compose; routes API calls to Node.js container |
| Postman | API testing | Latest | Unit and integration testing of all REST endpoints during Node.js and FastAPI development; automated test collection for regression testing |

## 3.6 System Implementation

System implementation proceeded in four sequential phases, each producing a testable artefact validated before the next phase began. This iterative generate-test cycle is the operational expression of the DSR methodology described in Section 3.1.

### 3.6.1 Phase 1: Simulation Engine and Dataset Generation

Phase 1 developed the Python simulation engine and generated the 30-day training dataset. The simulation engine comprises of four modules namely the irradiance model which applies a sinusoidal diurnal profile with randomised cloud cover events parameterised by time-of-year, the battery discharge model that uses published voltage-capacity discharge curves for both lead-acid and LiFePO4 chemistry, the inverter model applying efficiency de-rating under variable load, and the fault injection module which introduces five fault classes at configurable onset timestamps and severity levels. Validation compared generated voltage-current-irradiance relationships against expected physical behaviour before Gaussian noise injection that is PV current peaks within 20% of solar noon on clear-sky days, battery voltage follows its discharge curve within ±3%, inverter efficiency holds within ±5% across the load range. Parameters were tuned iteratively until generated data matched published curves within these tolerances.

### 3.6.2 Phase 2: Hardware Simulation, Assembly, and Firmware Development

Prior to physical breadboard assembly, the edge node architecture was modelled and simulated using Wokwi, a cloud-based Electronic Design Automation (EDA) and IoT simulation platform. Traditional SPICE simulators (e.g., Proteus) are structurally limited in evaluating modern IoT systems because they cannot natively execute FreeRTOS environments or simulate live 802.11 Wi-Fi and MQTT network stacks. Wokwi was selected because it compiles the actual C++ ESP32 firmware and executes it within a virtualised network environment. The physical I2C (DS3231) and 1-Wire (DS18B20) interfaces were mapped, while the proprietary ACS712 and PZEM-004T modules were electrically simulated using variable analog voltage dividers and UART serial generators to validate the microcontroller’s ADC and serial parsing logic.

Figure 3.5: Wokwi virtual circuit schematic demonstrating ESP32 I2C, ADC, and UART proxy sensor integration prior to physical assembly.

Following successful virtual validation of the circuit and MQTT payload construction, the system was translated to a physical breadboard prototype. The firmware was developed in C++ using PlatformIO and organised as five sequential tasks executed on a FreeRTOS five-minute timer that is sensor reading (PZEM-004T via UART, ACS712 via ADC with auto-zero offset applied, BH1750 via I2C, DS18B20 via 1-Wire, DS3231 via I2C for timestamp), JSON payload construction (all six sensor values, DS3231 timestamp, and a voltage-derived SoC estimate), MQTT transmission attempt (QoS 1 to broker, on connection failure payload is written to LittleFS) and LittleFS buffer flush (on each successful MQTT connection and the buffered records read and transmitted in chronological order before real-time resumption); and ACS712 auto-zero recalibration.

Figure 3.6: Simulated firmware execution verifying JSON telemetry payload construction, network resilience, and MQTT QoS 1 publication.

A separate DS3231 auto-sync routine runs on each Wi-Fi connection event that is on successful NTP synchronisation, the firmware writes the NTP-derived Unix timestamp to the DS3231 via I2C thus it keeps the RTC aligned with UTC whenever the network is available. On any reboot without connectivity, the firmware reads the DS3231 immediately and uses that timestamp for all records until NTP is restored. This ensures that every record buffered in LittleFS during an outage carries an accurate, monotonically increasing absolute timestamp.

### 3.6.3 Phase 3: Machine Learning Model Training

Phase 3 trained and evaluated both ML models using the simulation dataset. Training was executed in a Jupyter Notebook environment for iterative parameter exploration, then refactored into a standalone Python training script for reproducible production use. The Random Forest Regressor was trained with n_estimators=200, max_features='sqrt', and minimum node impurity tuned via five-fold cross-validation on the 70% training partition. Feature importance rankings were extracted post-training that is battery terminal voltage, ambient temperature, and battery discharge current ranked as the three highest-weight features for SoH prediction, consistent with the electrochemical mechanisms of capacity fade under thermal and cycling stress. This interpretability output is exposed on the React dashboard model health panel, enabling the operator to understand which sensors are most diagnostically relevant.

The Isolation Forest was trained on the normal-operation class of the training partition (85% of training records), with contamination=0.01. Anomaly scores were cross-validated against the fault-class records in the training partition, confirming that the contamination threshold correctly separated injected fault signatures from normal operational variation before evaluation on the held-out test set. Both models were serialised using joblib and placed in the FastAPI microservice's models/ directory for in-memory loading at service startup. To bridge the sim-to-real gap before fault-injection evaluation, a 12-to-24-hour normal-operation baseline will be recorded from the physical test circuit before any faults are injected. These real-hardware records will be appended to the Isolation Forest’s training data, anchoring the anomaly boundary to the specific electrical characteristics of the laboratory test rig rather than the mathematically idealised simulation alone.

### 3.6.4 Phase 4: Backend, Dashboard, and Docker Integration

Phase 4 developed the Node.js/Express telemetry service, the Python/FastAPI inference service, the MySQL schema, and the React PWA dashboard, then integrated all four into a single Docker Compose configuration. The MySQL schema was designed with four tables namely telemetry (raw sensor records with DS3231 timestamps and a record_source field distinguishing real-time from Store-and-Forward records), inference_results (per-record SoH percentage and anomaly score, foreign-keyed to telemetry), alerts (fault notifications with severity classification, timestamp, and triggered-feature values), and calibration_log (RMSE, MAE, and timestamp for each model recalibration event, providing the empirical basis for concept drift monitoring).

The Docker Compose file defines three services that is the node_api, fastapi_ml, and mysql_db on a shared bridge network named predictive_grid, with a named MySQL data volume ensuring database persistence across container restarts, an Nginx container serving the built React PWA as static files, and health checks on all three services to prevent the Node.js container from starting before MySQL is accepting connections. This configuration was validated on the development laptop and confirmed to reproduce identically on Docker-enabled ARM64 hardware (Raspberry Pi 4) and AMD64 cloud VMs, as expected from Docker's multi-platform architecture (Docker Documentation, 2025).

## 3.7 System Testing and Evaluation

### 3.7.1 Unit Testing

Each system module was tested independently before integration. ESP32 firmware was verified using the Arduino Serial Monitor that is the PZEM-004T voltage readings were compared against a calibrated digital multimeter reference (target: within ±0.5% of reference), ACS712 readings were compared against a known DC source from a laboratory power supply (target: within ±1.5% at 25°C), BH1750 readings were compared against a reference lux meter under identical illumination (target: within ±5 lux); DS3231 timestamps were verified against NTP reference over 48 hours of disconnected operation (target: drift under ±2 seconds/day). Node.js and FastAPI endpoints were tested using Postman and all REST routes were verified to return correct HTTP status codes, JSON response structures, and error codes for malformed input payloads.

### 3.7.2 Integration Testing

Integration testing verified correct data flow through the complete pipeline. With known input values injected at the ESP32 level, output values were inspected at each pipeline boundary that is MQTT payload structure and QoS acknowledgement, Node.js receipt and MySQL write confirmation, FastAPI inference return value and MySQL inference_results record, WebSocket broadcast to the React client; and dashboard display rendering. The integration test specifically confirmed that DS3231 timestamps survived the full pipeline without format conversion errors, that inference results correctly referenced their originating telemetry records by primary key, and that the React dashboard displayed updated values within 5 seconds of sensor reading.

### 3.7.3 Fault Injection Testing

Fault injection testing evaluated predictive and detection capabilities against five physical scenarios. Table 3.4 specifies each scenario, its implementation method, the expected ML system response, and the quantitative pass criterion. The scenarios cover the three fault categories defined by Kull et al. (2025), namely DC-side faults (Scenarios F3 and F5), AC-side faults (Scenario F2), environmental degradation (Scenario F1), and architectural resilience (Scenario F4).

Table 3.4: Fault Injection Scenarios, Physical Implementation, and Pass Criteria

| Fault Scenario | Physical Implementation | Fault Class (Kull et al., 2025) | Expected ML Response | Pass Criterion |
| --- | --- | --- | --- | --- |
| F1: Partial panel shading | BH1750 physically obstructed at 25%, 50%, 75% opacity using layered translucent film; irradiance drops while ambient temperature holds steady | Environmental partial shading | Isolation Forest anomaly score exceeds contamination threshold within 2 logging intervals (10 min); RF SoH estimate unaffected (irradiance feature weighted separately) | Anomaly correctly flagged; SoH model does not misclassify irradiance drop as battery fault |
| F2: Inverter overload | Resistive load bank increased in 10% increments beyond rated inverter capacity; PZEM-004T monitors output power deviation | AC-side inverter thermal stress | Isolation Forest detects abnormal power-to-irradiance ratio deviation; output power feature drives anomaly score above threshold | Alert generated before physical overload protection trips; logged to MySQL alerts table with correct fault category |
| F3: Battery deep discharge | Resistive load sustained until battery terminal voltage drops below DoD threshold (11.5V lead-acid / 10% SoC) | DC-side battery deep cycling / degradation | RF SoH estimate drops below 80% warning zone; IF flags abnormal discharge rate relative to load profile baseline | Battery health alert raised and persisted; voltage-SoC correlation correctly reflected in SoH output |
| F4: Network outage — Store & Forward | Wi-Fi router powered off for 4 hours; ESP32 continues 5-min logging; DS3231 provides timestamps throughout; router restored; buffer flushes | N/A, architectural resilience test | LittleFS buffers 48 records; DS3231 timestamps all records correctly; MQTT QoS 1 transmits batch in chronological order on reconnection | PDR = 100% (zero records lost); all 48 timestamps monotonically correct; MySQL receives complete 4-hour data block with no epoch-time entries |
| F5: ACS712 open circuit (sensor fault) | ACS712 signal wire disconnected mid-session while other sensors continue reading normally | DC-side, sensor fault (open circuit) | IF detects step-change anomaly in current channel; current drops to zero while voltage and power hold expected values — unmistakable multi-parameter deviation | Fault isolated within 1 logging interval (5 min); system continues operating; subsequent records resume correctly after reconnection; no firmware crash |

Scenario F4, the network outage test, is the most architecturally critical evaluation in this study. The Wi-Fi router is powered off for exactly 4 hours while the ESP32 continues logging at five-minute intervals, producing 48 records that must be buffered to LittleFS with DS3231 timestamps and transmitted in chronological order with zero data loss on router restoration. The pass criterion of PDR = 100% and monotonically correct timestamps directly validates the three-layer data integrity architecture against the vulnerability documented in Nassar et al. (2024), where data was permanently lost during connectivity failures.

### 3.7.4 Evaluation Metrics

System performance is quantified using eight metrics covering both ML evaluation and network engineering standards and the standardized ML performance indicators established for solar PV diagnostics by Vichare and Gaikwad (2025). Table 3.5 defines each metric, its formula, and its interpretation in this study.

Table 3.5: Evaluation Metrics, Formulae, and Performance Targets

| Metric | Category | Formula | Interpretation and Target |
| --- | --- | --- | --- |
| RMSE | ML regression | √(Σ(ŷ − y)² / n) | Primary accuracy metric for Random Forest SoH regression. Penalises large errors proportionally. Target: RMSE < 5% SoH units, consistent with literature benchmarks for field-deployed battery health estimation |
| MAE | ML regression | Σ¦ŷ − y¦ / n | Complements RMSE; less sensitive to outliers. Provides a second accuracy confirmation for the RF model on the 30% held-out test partition |
| Precision | ML classification | TP / (TP + FP) | Fraction of Isolation Forest anomaly alerts that correspond to genuine injected fault events. High precision reduces alert fatigue which is critical for an operator who must act on every notification |
| Recall (Sensitivity) | ML classification | TP / (TP + FN) | Fraction of the five injected fault scenarios that the IF correctly detected. High recall ensures no genuine fault event is missed during the evaluation window |
| F1-Score | ML classification | 2 × P × R / (P + R) | Harmonic mean of Precision and Recall. Primary classification metric for Isolation Forest given the inherent class imbalance in anomaly datasets (~1% fault rate per Kabir et al., 2023). Target: F1 > 0.90 |
| Packet Delivery Ratio (PDR) | Network resilience | Records in MySQL / Records buffered in LittleFS × 100% | Quantifies the Store and Forward mechanism's data integrity during the 4-hour network outage simulation. Target: PDR = 100.0% (zero record loss) |
| End-to-End Latency | System engineering | t_alert − t_sensor (seconds) | Elapsed time from physical sensor reading to React dashboard alert notification. Measured across 10 consecutive readings. Target: < 30 seconds at five-minute logging interval |
| Baseline Comparison | Comparative analysis | IF detection count vs. static threshold detection count on identical fault dataset | Demonstrates the added diagnostic value of ML over the fixed-threshold approach documented in Nassar et al. (2024). IF should detect F1 (partial shading) and F5 (sensor fault) that the static threshold misses entirely |

The static-threshold baseline comparison runs the Nassar et al. (2024) approach which fixed voltage and power thresholds with no ML inference against the same fault injection dataset used to evaluate the Isolation Forest. The number of fault events correctly identified by the static approach is recorded and contrasted with the IF detection rate, providing a quantitative demonstration of the added diagnostic value of ML over the best-documented comparable system in the literature.

## 3.8 Ethical Considerations

This research operates entirely within a controlled university laboratory environment using a low-voltage test circuit below 50V DC, in compliance with the undergraduate engineering safety protocols of Chinhoyi University of Technology. No human participants are involved at any stage of data collection. All sensor data acquired during prototype testing is engineering measurement data, voltage, current, temperature, and illuminance from a physical test circuit, and does not constitute personal data under any applicable data protection framework.

The synthetic dataset used for ML model training was generated entirely by the simulation engine described in Section 3.4.2 and contains no data from real individuals or organisations. All academic sources cited in this study were accessed through legitimate scholarly databases. The system's ML models are interpretable; namely, the Random Forest feature importance rankings are fully auditable and are surfaced on the dashboard, ensuring no unexplainable automated decisions are made in the fault alert generation logic.

For any commercial deployment beyond the scope of this research, the modular architecture supports the addition of HTTPS/TLS 1.2 encryption, MQTT broker client authentication and access control lists, Role-Based Access Control at the Node.js API layer, and encrypted credential storage in the ESP32's hardware eFuse module, as discussed in Chapter 2, Section 2.5.5. These extensions are acknowledged as necessary for production systems handling operational data from paying clients, but fall outside the scope of the proof-of-concept validation conducted in this study.

## 3.9 Limitations of the Methodology

- The synthetic training dataset, while augmented with hardware-calibrated Gaussian noise, cannot fully replicate the non-linear, long-term degradation patterns of batteries that have cycled in the field for multiple years under real ambient conditions. The continuous operational data logging design partially addresses this over time, but the initial model deployment relies on simulation-derived weights.

- Physical hardware testing uses 12V 7Ah sealed lead-acid batteries which is a scaled-down representation of the 100Ah to 200Ah banks typical in household solar installations. Voltage-current-temperature relationships scale predictably, but thermal dynamics and degradation rates at larger capacity may differ. Direct quantitative transfer of RMSE results to full-scale deployments requires field revalidation.

- The laboratory test environment maintains ambient temperatures between 20–28°C. The ACS712 temperature-dependent drift and battery electrochemical behaviour at Zimbabwe's summer peaks of 38–42°C cannot be fully replicated. The auto-zero calibration routine addresses sensor drift, but battery thermal dynamics under high ambient temperatures are not captured in the laboratory evaluation.

- The development laptop server runs considerably more RAM and CPU cores than the Raspberry Pi 4 production target (8GB RAM and eight cores vs. 4GB RAM and four ARM Cortex-A72 cores). Inference latency measured on the laptop will be lower than on the Pi 4. Since Random Forest and Isolation Forest inference on CPU-only hardware runs well under 50 milliseconds per record, the performance margin is sufficient to absorb the Pi 4's slower processing without violating the 30-second end-to-end latency target.

- The five-minute logging interval balances data granularity against LittleFS storage capacity and MQTT bandwidth. Transient fault events that develop and resolve within a single logging window, such as brief inverter load spikes, may be missed at this interval. A one-minute interval would improve transient detection, but increases daily flash write frequency by five times and proportionally increases MQTT bandwidth requirements.

## 3.10 Chapter Summary

This chapter presented the research methodology used to design, develop, and evaluate the predictive maintenance prototype. The study adopts a Design Science Research approach (Hevner et al., 2004), combining computer simulation for dataset generation with experimental prototyping for hardware validation. The six DSR stages were mapped to specific research activities and deliverables in Table 3.1.

The system architecture was presented as a five-layer IoT structure (Al-Fuqaha et al., 2015) in Figure 3.1, with each layer's design decisions justified by quantified engineering evidence: namely, ESP32 active draw of 160mA against Raspberry Pi 4's 500–600mA idle, LittleFS copy-on-write resilience over deprecated SPIFFS (Espressif Systems, 2024), Node.js/FastAPI microservices separation preventing ML computation from blocking telemetry ingestion, and Docker Compose containerisation enabling laptop PoC to production deployment without code changes (Docker Documentation, 2025; Hashim et al., 2025). The ML data pipeline was diagrammed in Figure 3.2, the hardware connection block diagram in Figure 3.3, and the Store and Forward firmware state machine in Figure 3.4. Hardware components were specified in Table 3.2 with datasheet-backed justifications. Software tools were listed in Table 3.3. The four implementation phases were described with their specific validation steps. Fault injection scenarios were specified with pass criteria in Table 3.4, and evaluation metrics were defined with targets in Table 3.5. The next chapter presents the implementation results, dataset analyses, and performance evaluation outcomes.

# REFERENCES

Abdulla, H., Sleptchenko, A., & Nayfeh, A. (2024). Photovoltaic systems operation and maintenance: A review and future directions. Renewable and Sustainable Energy Reviews, 195, Article 114720. https://doi.org/10.1016/j.rser.2024.114720

Ahmed, A. M., Li, L., & Khalilpour, K. (2025). Predictive maintenance of solar photovoltaic systems: A comprehensive review. IET Renewable Power Generation, 19(1), 1–34. https://doi.org/10.1049/rpg2.70152

Al-Fuqaha, A., Guizani, M., Mohammadi, M., Aledhari, M., & Ayyash, M. (2015). Internet of things: A survey on enabling technologies, protocols, and applications. IEEE Communications Surveys & Tutorials, 17(4), 2347–2376. https://doi.org/10.1109/COMST.2015.2444095

Alcalá-Rodríguez, U. E., et al. (2025). Development and evaluation of solar radiation sensor using cost-effective light sensors and machine learning techniques. Technologies, 13(5), 182. https://doi.org/10.3390/technologies13050182

Allegro MicroSystems. (2024). ACS712: Fully integrated, Hall-effect-based linear current sensor IC with 2.4 kVRMS isolation (Rev. 22) [Datasheet]. Allegro MicroSystems, LLC. https://www.allegromicro.com/en/products/sense/current-sensor-ics/acs712

Breiman, L. (2001). Random forests. Machine Learning, 45(1), 5–32. https://doi.org/10.1023/A:1010933404324

DEV Community. (2025). Node.js vs Python: Performance comparison for backend development. DEV Community. https://dev.to

Docker Documentation. (2025). Multi-platform builds. Docker, Inc. https://docs.docker.com/build/building/multi-platform/

Espressif Systems. (2024). File system considerations, ESP32 ESP-IDF programming guide (v5.5). Espressif Systems. https://docs.espressif.com/projects/esp-idf/en/stable/esp32/api-guides/file-system-considerations.html

Fortune Business Insights. (2024). SCADA market size, share & industry analysis. Fortune Business Insights Research Report.

Fracttal Tech S.L. (2026). Predictive maintenance in solar power plants. Fracttal Insights.

Hamasha, M. M., Albedoor, Q., Hamasha, S., Ali, H., Qamar, A., & Berrah, F. (2025). A comprehensive framework for IoT-driven predictive maintenance: Leveraging edge computing for enhanced equipment reliability. Journal of Applied Engineering Science, 23(3), 471–486. https://doi.org/10.5937/jaes0-57002

Hashim, A., et al. (2025). Exploring dynamic RESTful API implementation in IoT environments using Docker. Scientific Reports, 15, Article 33278. https://doi.org/10.1038/s41598-025-16460-0

Kabir, S., Shufian, A., & Zishan, M. S. R. (2023). Isolation forest based anomaly detection and fault localization for solar PV system. In Proceedings of the 3rd International Conference on Robotics, Electrical and Signal Processing Techniques (ICREST 2023) (pp. 341–345). IEEE. https://doi.org/10.1109/ICREST57604.2023.10070033

Kull, K., Asad, B., Khan, M. A., Naseer, M. U., Kallaste, A., & Vaimann, T. (2025). Faults, failures, reliability, and predictive maintenance of grid-connected solar systems: A comprehensive review. Applied Sciences, 15(21), 11461. https://doi.org/10.3390/app152111461

Last Minute Engineers. (2024). Getting date and time from NTP server with ESP32. Last Minute Engineers. https://lastminuteengineers.com/esp32-ntp-server-date-time-tutorial/

Ledmaoui, Y., El Maghraoui, A., El Aroussi, M., & Saadane, R. (2025). Review of recent advances in predictive maintenance and cybersecurity for solar plants. Sensors, 25(1), 206. https://doi.org/10.3390/s25010206

Liu, F. T., Ting, K. M., & Zhou, Z.-H. (2008). Isolation forest. In Proceedings of the 8th IEEE International Conference on Data Mining (ICDM 2008) (pp. 413–422). IEEE. https://doi.org/10.1109/ICDM.2008.17

Marangis, G., Kaliampakos, D., & Benardos, A. (2025). Intelligent maintenance approaches for improving photovoltaic system performance and reliability. Solar RRL. https://doi.org/10.1002/solr.202500289

Mehta, K., Lwakatare, B., Zörner, W., et al. (2025). Mini-grid performance in Sub-Saharan Africa: Case studies from Tsumkwe and Gam, Namibia. Sustainable Energy Research, 12, 30. https://doi.org/10.1186/s40807-025-00174-y

Mellit, A., Benghanem, M., Kalogirou, S., & Massi Pavan, A. (2023). An embedded system for remote monitoring and fault diagnosis of photovoltaic arrays using machine learning and the internet of things. Renewable Energy, 208, 399–408. https://doi.org/10.1016/j.renene.2023.03.015

Michael, P. R., Johnston, D. E., & Moreno, W. (2020). A conversion guide: Solar irradiance and lux illuminance. Journal of Measurements in Engineering, 8(4), 153–166. https://doi.org/10.21595/jme.2020.21667

Ministry of Energy and Power Development. (2025). Zimbabwe energy sector report 2025. Government of Zimbabwe.

Nassar, Y. F., El-Khozondar, H. J., Mtair, S. Y., Qoffa, K. O., Qasem, O. I., & Munyarawi, A. H. (2024). Development of a low-cost monitoring device for solar electric (PV) system using internet of things (IoT). Results in Engineering, 24, Article 103024. https://doi.org/10.1016/j.rineng.2024.103024

Patabo, M. D., Daud, J. G., Ponnokaraeng, S. I., Tongkotou, G., Kapoh, I. T., & Sariowan, Y. L. G. (2024). Maintenance of solar power plants for household electricity use. Syntax Admiration, 5(12), 5897–5903.

PCB Artists. (2024). ESP32 NTP and DS3231 RTC: Accurate timekeeping for IoT applications. PCB Artists. https://pcbartists.com/firmware/esp32-firmware/esp32-ntp-and-ds3231-rtc/

PEACEFAIR. (2023). PZEM-004T V3.0 user manual: AC communication module. PEACEFAIR.

Pillai, P. K., Devaraj, D., & Selvam, S. (2025). Smart diagnostics of AI-powered IoT solutions for solar grid reliability. Discover Electronics, 2(72). https://doi.org/10.1007/s44291-025-00113-7

Raijmakers, L. H. J., Danilov, D. L., & Notten, P. H. L. (2022). Online internal temperature sensors in lithium-ion batteries: State-of-the-art and future trends. Frontiers in Chemical Engineering, 3, Article 804704. https://doi.org/10.3389/fceng.2022.804704

Random Nerd Tutorials. (2024). ESP32 guide for DS3231 real time clock module (RTC). Random Nerd Tutorials. https://randomnerdtutorials.com/esp32-ds3231-real-time-clock-arduino/

Raspberry Pi Ltd. (2025). Raspberry Pi 4 model B. Raspberry Pi Ltd. https://www.raspberrypi.com/products/raspberry-pi-4-model-b/

Sigma Technology. (2025). Exploring predictive maintenance in renewable energy. Sigma Technology Insights.

Shukla, A. (2026). Artificial intelligence-driven monitoring and predictive maintenance in floating solar power plants: A comprehensive review. International Journal of Research & Technology, 14(1). https://ijrt.org/j/article/view/988

SolarPower Europe. (2025). Global market outlook for solar power 2025–2029. SolarPower Europe Publications.

Tasmant, H., et al. (2025). A review of machine learning and IoT-based energy management systems for AC microgrids. Computers and Electrical Engineering, 127, 110563.

Topalović, D., et al. (2024). Analysis of using machine learning techniques for estimating solar panel performance in edge sensor devices. Applied Sciences, 14(3), 1296. https://doi.org/10.3390/app14031296

Veritas Zimbabwe. (2025). Economic governance watch 01-2025: The energy crisis — need to re-look at the energy mix. Veritas Zimbabwe.

Vichare, R. V., & Gaikwad, S. R. (2025). AI-based predictive maintenance of solar photovoltaics systems: A comprehensive review. Energy Informatics, 8(128). https://doi.org/10.1186/s42162-025-00594-6

ZERA (Zimbabwe Energy Regulatory Authority). (2024/2025). Renewable energy regulations and framework. ZERA Publications.

Hevner, A. R., March, S. T., Park, J., & Ram, S. (2004). Design science in information systems research. MIS Quarterly, 28(1), 75–105. https://doi.org/10.2307/25148625