# Machine Learning Based Predictive Maintenance System for Solar Mini-Grids

Takudzwa Kelvin Mukaro

C21145793S

Chinhoyi University of Technology

Department of ICT and Electronics

This project is submitted in partial fulfillment of the requirements for the Bachelor of Engineering Honours Degree in Computer Engineering.

## DEFINITION OF KEY TERMS

## URL- Universal Resource Locator

## ICT-Information Communication Technology

## QAT- Quality Assurance Test

## IP- Internet Protocol

ML- Machine Learning

IoT- Internet of Things

Abstract

Solar mini-grids are being highly adopted in developing countries to address grid instability(causing load sheding) and rural electrification needs. However, these systems frequently suffer from unexpected failures due to a lack of automated monitoring and predictive maintenance mechanisms. This research developed a machine learning-based predictive maintenance system to monitor, detect, and predict faults in solar mini-grid’s components. The main goal was to reduce system downtime and increase the lifespan of components by early fault detection. The research used an experimental approach, integrating Internet of Things (IoT) technologies with Machine Learning (ML) algorithms. I planned a prototype for data acquisition node using ESP32 microcontrollers to take real-time working parameters, including battery voltage, current, inverter load, and surrounding temperature. A synthetic dataset for 30 days of mini-grid operation was generated so as to train two ML models, namely Random Forest Regression for battery health prediction and Isolation Forest for anomaly detection. I developed a full-stack web application using Node.js for backend and React for the frontend to visualize the system’s performance and alert users to faults. The Random Forest model got a prediction accuracy more than 99% for battery health estimation. The Isolation Forest algorithm successfully recognized inserted anomalies, such as inverter overloads and solar panel underperformance, with low delay. The system confirmed its capability as a low cost and intelligent monitoring tool in real-time visualization (frontend dashboard) and sending alert notifications to the user. Integrating ML with low-cost IoT sensors can enhance the reliability, efficiency, and sustainability of solar mini-grids in resource-limited environments, thus the conclusion of this research.

# CHAPTER 1: INTRODUCTION

## 1.1 Introduction

Everyone talks about the solar revolution, but few discuss what happens after the panels go up. The critical question remains: who fixes the inverter when it fails, and who keeps the current flowing when the closest engineer is 200 kilometers away? In rural communities across Africa, Asia, and Latin America, thousands of solar mini-grids now power homes, schools, and small businesses. They act as symbols of hope and proof that clean energy can reach the “last mile”. But beneath that progress lies a fragile truth: a system is only as strong as the people using it and the tools available to maintain it.

According to Yann Doignon Sirven (June 2025), energy is now the lifeblood of economic development and social progress. He also stated that hospitals, businesses, and mostly students cannot study after dark without using energy. Having reliable and affordable energy can improve living standards, protect essential services, create jobs, drive digitalization for everyone, and push growth. Many developing nations, including Zimbabwe, have faced significant challenges regarding reliable electricity supply, which is characterized by frequent grid outages and rising utility costs. In response to this, there has been a rapid adoption of renewable energy solutions, with solar mini-grids as the most popular for rural and urban electrification and industrial sustainability.

However, the use of these systems has improved faster than the development of effective maintenance strategies. Traditional maintenance ways remain largely reactive, where repairs are only conducted after a failure has occurred. This "run-to-failure" model is not efficient, costs a lot, and is not beneficial to the long-term reliability of solar energy. The research attempts to solve these problems by integrating a Machine Learning Based Predictive Maintenance System to monitor, analyze and detect faults before they happen in solar mini-grids (Akyaz & Engın, 2024).

## 1.2 Background of the Study

Zimbabwe’s demand for power has outgrown the supply and is resulting in loadshedding. This shortage has forced households, farmers, and Small-to-Medium Enterprises (SMEs) to invest in solar photovoltaic (PV) systems. Solar energy offers a clean and decentralized alternative, but the systems themselves are very complex, including sensitive components such as PV panels, inverters, and battery storage banks.

Regardless of the high initial investment required for these systems, most mini-grids lack automated monitoring and maintenance mechanisms. Users only rely on manual inspections which are infrequent, prone to human error, and unable to detect internal component degradation until it is too late. Scheduled visual inspections mostly miss common issues like deterioration of the battery, inverter overloads sometimes, partial shading of panels, and abnormal temperatures.

When these faults happen the system can fail completely, and the consequences are very severe, from unexpected downtime to expensive emergency replacements and safety risks such as battery fire. Adding to that, public trust in solar systems is lost. It is now possible to shift from reactive maintenance to predictive maintenance by using low-cost IoT sensors and AI, specifically ML. Intelligent systems can now identify possible failures by evaluating real-time operational data thus allowing cost-effective actions that ensure supply continuity.

## 1.3 Statement of the Problem

Since the development of solar mini-grids, they have suffered worse than expected performances and sudden malfunctions due to lack of active monitoring and predictive maintenance systems. The use of scheduled manual and reactive maintenance causes serious problems, such as:

- Unexpected Downtime: Systems can fail without giving a warning thus disrupting critical activities for users.

- Reduced Component Lifespan: Abnormal charging/discharging of solar batteries and overheating in inverters can degrade these components quickly if not corrected immediately.

- High Operational Costs: Preventative maintenance is much more cheaper than emergency repairs or to some extent component replacements.

- Lack of Visibility: In areas like rural areas, the users lack technical expertise near them to even identify root causes of underperformance.

This research aims to cover this gap by implementing a low-cost machine learning predictive maintenance system since there is currently no affordable, automated and intelligent tool locally that can address these failures and give alerts in real-time.

## 1.4 Aim and Objectives

### 1.4.1 Main Objective

To design and implement a predictive maintenance system using Machine Learning and IoT sensors that is able to monitor, detect and predict faults in solar mini-grids.

### 1.4.2 Specific Objectives

## The study aimed at a number of objectives to achieve our main objective and below are the specific objectives:

- To simulate and generate an operational dataset for solar mini-grids that includes PV output, inverter load, battery voltage, and temperature parameters so that we establish baseline behavior.

- To do feature engineering on these parameters and also store in the same dataset.

- To collect real-time measurements from system components using IoT data collection module with ESP32 microcontrollers.

- To train Random Forest model for battery health prediction.

- To train Isolation Forest model for anomaly detection.

- To develop a nodejs backend system that handles operations and a React dashboard with real-time monitoring, visualization, and can raise alert notifications.

- To study accuracy metrics, the prediction error and the system's responsiveness under changing working conditions so that we can evaluate the system's performance.

## 1.5 Significance of the Study

This system is of great importance to a lot of stakeholders in the energy sector due to significant operational, economic and policy-related benefits if it is to be implemented successfully such as:

- Operational Efficiency: The system reduces downtime and ensures reliable supply of power.

- Cost Reduction: Being alert for future faults help save costs for users because they will have planned maintenance.

- Extended Component Life: Continuous monitoring of components extends lifespan, for example, the continuous monitoring of battery health prevents abusive usage patterns like deep cycling.

- Contribution to Research: This study can provide help and insights to the body of knowledge on smart energy management and the application of AI in renewable energy within the Zimbabwean context and predictive maintenance systems in general.

- Scalability: This system is built in modules, thus making it scalable and adaptable.

## 1.6 Scope and Delimitations

### 1.6.1 Scope

The major goal of the project was to create a prototype for predictive maintenance for standalone solar mini-grids. It included choosing and implementation of sensor nodes for voltage, current and temperature, implementing ML models namely Random Forest and Isolation Forest algorithms, and the development of a web-based monitoring dashboard

### 1.6.2 Delimitations

- Data Simulation: Long-term historical data was not collected due to time constraints of the project, and instead, simulated and synthetic datasets were used to train machine learning models and model system behavior.

- Prototype Hardware: Instead of a high-voltage industrial deployment our prototype was          limited to the laboratory so as to reduce risks and costs and just prove the proof of concept.

1.7 Limitations

- Hardware Availability: Low cost sensor alternatives were considered for the prototype due to budget and availability constraints.

- Environmental Variations: While the simulation accounted for real-world weather conditions like cloud cover and ambient heat to be varying unpredictably, the prototype testing was laboratory controlled.

- Training Data: The lack of years of historical data for local mini-grids limited the ability to train for long-term seasonal degradation patterns since Machine Learning models depend on large volumes of data.

## 1.8 Definition of Terms

- Predictive Maintenance:  It is a proactive way that works by capturing and analyzing equipment data in real time to predict potential issues before they lead to equipment failure.

- Solar Mini-Grid: It is an independent energy system that ranges from a few kilowatts to 10 megawatts and uses solar panels to generate and battery as storage to provide electricity.

- Internet of Things (IoT): A network of physical objects, "things" that are embedded with sensors, software, and other technologies so as to connect and exchange data with other devices and systems over the internet.

- Machine Learning (ML): A subset of artificial intelligence that enables the training of algorithms to learn patterns from data and make predictions or decisions without being explicitly programmed.

- Anomaly Detection: The process of identifying rare items, events, or observations that deviate significantly from a dataset's established normal behavior or baseline.

## 1.9 Chapter Summary

This opening chapter laid the groundwork for our exploration from the origins of the project, the specific challenge it aims to solve, and what we hope to achieve. Another key part of chapter one was underscoring how this maintenance system can increase reliability of solar mini-grids.

# CHAPTER 2: LITERATURE REVIEW

## 2.1 Introduction

A literature review is a scholarly article that provides background information and evidence of the author's familiarity with the academic literature on a particular topic. The reason it is regarded as a literature review instead of a literature report is that it includes an evaluation of the sources critically. It is an approach to reading and writing literature. This chapter reviews prior research as well as the conceptual framework that offers a schematic relationship between the variables being studied.

Examining the studies that are now available from other academics and researchers who have worked on the same field of study is the goal of the review. The literature review will act as a guide for this inquiry to avoid repeating earlier work.

To build an effective predictive maintenance system, one must first understand the operational nuances of the systems being monitored. This chapter explores the theoretical framework surrounding solar photovoltaic (PV) mini-grids, specifically focusing on how they function and, more importantly, how they fail and all the faults associated with them. It further examines the technological bridge between hardware and software, the Internet of Things (IoT) and evaluates how Machine Learning (ML) algorithms are currently being deployed to predict equipment behavior. By reviewing previous attempts at solving these problems, this section identifies the specific technological gaps that justify the need for the low-cost, locally adaptable solution proposed in this study.

## 2.2 Operational Dynamics of Solar Mini-Grids

The term operational dynamics refers to the detailed, reat-time interaction between environment factors and the technical response of solar PV systems. To produce reliable power output and efficiency we must understand how these factors fluctuate dynamically since it is not enough to look at static ratings.

Environmental Feedbacks

The primary driver of any solar system is irradiance, which is the intensity of sunlight hitting the panels. While higher irradiance generally increases the flow of electrons, it often brings an unwanted side effect: heat. There is a non-linear relationship between light and temperature that creates a constant tug-of-war in system performance. As solar panels heat up, the semiconductor materials within them become less efficient, leading to a noticeable drop in output voltage. This phenomenon is defined by the panel’s "temperature coefficient," which typically results in an efficiency loss of roughly 0.3% to 0.5% for every degree Celsius that the cell temperature rises above the standard 25°C baseline.

Furthermore, the system must sort of compete with physical obstructions/effects. Dynamic shading effects can be produced by debris, dust buildup (soiling), or a cloud's shadow. These effects are out of proportion in conventional string inverter configurations which is connecting panels in series; if one panel is shaded, it becomes a botttleneck and reduces the system's output

Technical Control Mechanisms

To counter these environmental fluctuations, modern mini-grids employ active control logic. The most critical of these is Maximum Power Point Tracking (MPPT). The inverter constantly "hunts" for the optimal electrical load, the sweet spot where voltage and current multiply to give the highest possible wattage under the specific conditions of that moment.

Voltage regulation systems on the other hand use DC-DC converters to step up or stabilize voltage levels, making sure that even when solar intensity is low the power delivery stays constant. Charge controllers must dynamically control the current flowing into the battery which is closely related to energy storage management. Their role is to balance the load's demands and the need to protect the battery from overcharging during peak sun or deep discharging at night.


Mini-grids are prone to slow and unavoidable aging in addition to daily fluctuations. Due to UV exposure and thermal cycling these solar panels also degrade overtime naturally, typically losing about 0.5% of their efficiency per year. A reliable predictive maintenance system must be able to differentiate between acute faults that needs attention right away from this long term drift.

### 2.2.1 The Vulnerability of Core Components

While a standard setup for these solar mini-grids includes PV panels, inverters, and charge controllers, the Battery Energy Storage System (BESS) is often the single point of failure(SPOF). In Zimbabwe, Lead-Acid and Lithium-Ion batteries are the standard and the primary enemy of these batteries is "deep cycling", which means discharging the battery beyond its safe threshold. This physical stress degrades the battery's internal chemistry, reducing its capacity to hold a charge over time. We can also not run away from the fact that these batteries age, and this reduces the capacity. This aging is also increased by high temperatures and poor charging management. Incorrect BESS sizing or failure in the battery management system(BMS) can result in premature failure of the system.

Similarly, the inverter converts DC(stored energy) to AC(used by people) power, which is a very vulnerable part of a solar system. If the load exceeds the inverter's rating even for a few minutes, heat builds up in the semiconductor switches causing component degradation. Some solar systems are connected to the Grid and there are disturbances that happens in the grid that can cause inverters to disconnect or fail, which is called poor synchronization with the grid. Bugs in firmware, maximum power point tracking (mppt) failures can cause too much energy to be released or too little energy to be released, which can result in inverter failure.

For the solar panels themselves, issues are often environmental since they are exposed to harsh environments. Environmental degradation on solar panels includes accumulation of dust, dirt, bird droppings or even partial shading from a growing tree and these reduce sunlight absorption, whereby the partially shaded part acts as a resistor instead of a generator. High humidity, moisture ingress and salt spray in coastal areas can cause corrosion, layer separation, and damage to junction boxes. Very high temperatures, sudden change in temperatures and hail can cause micro-cracks in cells and broken glass also leading to reduced performance. These solar panels are also affected by electrical faults when there is a huge voltage difference between the cells and the grounded frame this leads to current leakages, ion migration and up to 30% power loss, this is called potential induced degradation. Severe weather conditions like cyclones, strong winds, lightning strikes can physically damage the structures and wiring. Solar flares can induce large currents in distribution lines, potentially damaging transformers this is called geomagnetic disturbances.

Modern day solar mini-grids are now relying on IT infrastructure which also brings in new vulnerabilities. Some researchers have found critical vulnerabilities in cloud infrastructure, monitoring, and communication dongles connecting inverters to the internet. This means lack of user verification in cloud platforms can lead to unauthorized access to inverters.

Lack of local technical expertise and the inability to replace parts in remote areas lead to small, repairable faults or failures becoming permanent inoperability. There is also misuse of the grid that is connecting high-load devices or power theft, which can overload the system and destroy components. Incorrectly estimated load profiles and poor initial sizing, in some cases up to 300% mismatch leads to system failure under demand.

### 2.2.2 The Shift from Reactive to Predictive Strategies

Traditionally, solar mini-grids have relied on fixing things when they break (reactive maintenance) or basic scheduled, routine checks (preventive maintenance). This results in high downtime due to unexpected failures in components, high costs on repairs and replacements, and operational inefficiency due to a lack of local expertise in remote areas resulting in prolonged downtime. This approach is inherently flawed because the damage has already been done. Research suggests that failures rarely happen suddenly but they have anomalies in the background like a slight dip in voltage or a temperature spike which are not always caught by manual inspections thus the need to monitor these anomalies and develop and predictive system.

Traditionally, these faults are handled "reactively." An operator waits for the lights to go out, then calls a technician.. Research suggests that catastrophic failures are rarely sudden; they are almost always preceded by subtle "anomalies"—a slight dip in voltage or a temperature spike—that manual inspections simply cannot catch. This reality drives the need for automated, continuous monitoring.

## 2.3 The Role of IoT in Modern Energy Systems

The Internet of Things (IoT) has fundamentally changed how we manage remote infrastructure. In the past, gathering data from a rural mini-grid meant physically sending a technician to read meters. Today, IoT allows us to create a "digital shadow" of the physical system.

For a project of this scale, the architecture is straightforward but powerful. Sensors act as the system's "nerves," feeling the voltage and heat. The microcontroller—in this case, the ESP32—acts as the local brain. The ESP32 is particularly favored in academic prototyping not just for its low cost, but because it handles two critical jobs simultaneously: it processes raw signals into meaningful data (Edge Computing) and transmits that data via Wi-Fi. This ability to process data "at the edge" is crucial when internet connectivity is spotty, as is often the case in rural Zimbabwe.

## 2.4 Machine Learning: The Engine of Prediction

Collecting data is useless if we cannot interpret it. This is where Machine Learning (ML) differentiates itself from standard software. Standard software follows fixed rules (e.g., "If voltage < 11V, sound alarm"), but it cannot spot complex, evolving patterns. ML models can.

### 2.4.1 Why Random Forest?

For predicting Battery Health, this study utilizes the Random Forest Regression algorithm. The choice is deliberate. Battery degradation is non-linear; it doesn't follow a straight line. Factors like temperature, discharge rate, and age all interact in complex ways. Random Forest works by creating hundreds of small "decision trees" and averaging their answers. This "wisdom of the crowd" approach makes it incredibly resilient to noise and prevents it from memorizing the training data (overfitting), which is a common pitfall in simpler models.

### 2.4.2 Why Isolation Forest?

For detecting Faults (Anomalies), the approach must be different. We often don't know what a new fault will look like until it happens. Therefore, we cannot train the model on every possible error. The Isolation Forest algorithm solves this by asking, "How easy is it to isolate this data point?" Normal data points are clustered together and hard to separate. An anomaly—like a sudden drop in PV output on a sunny day—stands out alone. This algorithm is computationally light and fast, making it ideal for detecting strange behavior in real-time without needing a supercomputer.

## 2.5 Review of Related Works

The concept of monitoring solar systems is not new, but previous solutions have often missed the mark for developing contexts.

For instance, Mellit and Pavan (2010) demonstrated that Artificial Neural Networks could detect faults with over 95% accuracy. While impressive, their system required high-performance computing hardware that is impractical for a low-budget rural installation. On the other end of the spectrum, Harb et al. (2020) built a low-cost Arduino system similar to the hardware proposed here. However, their system was purely a monitoring tool—it could tell you the current voltage, but it had no intelligence to predict future problems.

Another notable attempt by Garoudja (2017) used Support Vector Machines (SVM) effectively but focused entirely on the solar panels, neglecting the battery bank. In an off-grid setup, if the battery dies, the system is useless, regardless of how healthy the panels are.

## 2.6 The Research Gap

Reviewing the current landscape reveals a clear disconnect. We have high-end, intelligent systems that are too expensive for rural Zimbabwe, and we have low-cost hobbyist systems that lack the intelligence to be truly useful.

There is a distinct lack of a hybrid solution: a system that runs on cheap, accessible hardware (like the ESP32) but still possesses the advanced predictive capabilities of algorithms like Random Forest. This project aims to fill that specific gap, providing "First World" intelligence on "Third World" infrastructure constraints.

## 2.7 Chapter Summary

This chapter has framed the research within the broader context of renewable energy reliability. It established that while solar technology is mature, maintenance strategies are lagging. By leveraging the connectivity of IoT and the analytical power of Machine Learning, we can move from fixing broken systems to preventing them from breaking in the first place. The next chapter, Methodology, will detail exactly how this theory is translated into a working prototype.

References

Akyaz, T., & Engın, D. (2024). Machine learning-based predictive maintenance system for artificial yarn machines. IEEE Access, 12, 125446-125461. https://doi.org/10.1109/ACCESS.2024.3454548

Mellit, A., Pavan, A.M., Kalogirou, S.A. (2011). Application of Artificial Neural Networks for the Prediction of a 20-kWp Grid-Connected Photovoltaic Plant Power Output. In: Gopalakrishnan, K., Khaitan, S.K., Kalogirou, S. (eds) Soft Computing in Green and Renewable Energy Systems. Studies in Fuzziness and Soft Computing, vol 269. Springer, Berlin, Heidelberg. https://doi.org/10.1007/978-3-642-22176-7_10

A. Chouder and S. Silvestre, "Power loss analysis in photovoltaic systems through a monitoring approach," Sol. Energy, vol. 84, no. 3, pp. 326-336, 2010.

M. Dhimish, V. Holmes, B. Mehrdadi, M. Dales, and P. Mather, "Multiple fault detection and identification algorithm for photovoltaic systems," IEEE Trans. Device Mater. Reliab., vol. 18, no. 3, pp. 448-456, 2018.

E. Garoudja, F. Harrou, Y. Sun, K. Kara, A. Chouder, and S. Silvestre, "Statistical fault detection in photovoltaic systems using IoT-enabled monitoring," Sol. Energy, vol. 155, pp. 1090-1101, 2017.

K. A. Harb, A. Nuhic, M. C. E. Tano, and C. Batunlu, "Internet of Things based monitoring system for photovoltaic arrays," Renew. Energy, vol. 80, pp. 777-788, 2015.

Hopwood, M.W.; Patel, L.; Gunda, T. Classification of Photovoltaic Failures with Hidden Markov Modeling, an Unsupervised Statistical Approach. Energies 2022, 15, 5104. [Google Scholar] [CrossRef]

Bamisile, O.; Acen, C.; Cai, D.; Huang, Q.; Staffell, I. The environmental factors affecting solar photovoltaic output. Renew. Sustain. Energy Rev. 2025, 208, 115073. [Google Scholar] [CrossRef]

Anagbah, M.S.; Rawn, B. Solar Mini-Grid Planning Considerations for Future Central Grid Integration: A Case for Rwanda. In Proceedings of the 2023 IEEE AFRICON, Nairobi, Kenya, 20 September 2023; IEEE: Piscataway, NJ, USA, 2023; pp. 1–3. [Google Scholar]